# Step 7 — Workflow Design

Operational Technology Graduate Demonstration Project
Document: OT Project Workflow Design
Version: 0.4 (proposed)
Status: Draft — DC-006 authoritative-document application pending independent review; accepted baseline remains Workflow Design v0.3

# 1. Purpose

This document defines the controlled operational and engineering workflows for the Operational Technology Graduate Demonstration Project. It converts the approved System Architecture, 124 formal requirements and completed Network Model into exact actor, command, processing, decision, evidence and repeat-execution sequences for V1.

The Workflow Design establishes how a graduate engineer and simulated operator/reviewer progress through formal SEC-A2 validation, alarm handling, fault isolation, restoration assessment and execution, negative telemetry validation, Exploration Mode, seeded-defect investigation, correction, revalidation and evidence review. It does not select the technology stack or prescribe final screens; those matters belong to Step 8 — Demonstrator Design.

The purpose is to make implementation behaviour reviewable before code exists. A later interface may organise the work across different views, but it shall preserve the gates, records, sequence and engineering distinctions defined here.

## 1.1 Position in the Engineering Lifecycle

Step 7 sits between logical architecture and detailed demonstrator design. The Network Model remains the answer key for electrical state and calculated results. The System Architecture remains authoritative for component ownership and information boundaries. This document adds workflow meaning: who initiates an action, when it is available, what deterministic processing follows, what result is recorded and what evidence permits the next step.

## 1.2 Governing Authority and Change Boundary

Workflow choices are governed by the Project Vision, Project Definition and Project Decisions; the Engineering Design Brief, Requirements Specification and Network Model; accepted DC-001 and DC-002 changes; and the System Architecture. This document may resolve parameters explicitly deferred to Workflow Design, but it shall not silently change a requirement, network value, topology relationship or accepted scenario rule. Any such change requires controlled design change before downstream implementation.

# 2. Workflow Scope and Boundary

## 2.1 Included Workflows

- formal validation run initialisation from an approved test definition;

- the controlled SEC-A2 N0–N5 operational sequence;

- alarm presentation and acknowledgement without topology side effects;

- simulated fault-isolation and upstream-restoration switching;

- restoration-candidate discovery, permissive assessment and authorised simulated execution;

- stale, UNCERTAIN and BAD telemetry blocking behaviour, including a controlled stale-telemetry negative test;

- reviewer-selected Exploration Mode using corrected v1.1 configuration and the common scenario engine;

- formal expected-versus-observed comparison and immutable evidence capture;

- VT-TOP-DEF-001 execution against defective v1.0, investigation of DEF-001 and correction to v1.1;

- separate repeat validation, full N0–N5 regression and evidence assembly;

- reset and repeat semantics; and

- chronological operational events kept separate from formal engineering validation records.

## 2.2 Excluded Workflow Capabilities

- commands to real equipment, live SCADA, ADMS, OMS, GIS or utility networks;

- autonomous switching or an operational control-room procedure;

- automatic fault-location calculation, protection studies or detailed electrical fault types;

- free-form editing of formal expected results during execution;

- guaranteed restoration for every Exploration Mode fault selection;

- AI-assisted or automated engineering assurance features in V1;

- client approval, commissioning authority or production-grade safety claims; and

- final screen layout, navigation, storage technology or export-file selection.

## 2.3 Workflow States Are Not Screens

N0–N5 are engineering network states. Workflow stages such as INITIALISED, ACTIVE, ASSESSMENT_AVAILABLE, RUN_COMPLETE and EXECUTION_COMPLETED describe progress through a run or validation activity. A future screen may display more than one state or several screens may present one state; the implementation shall not encode engineering behaviour by assuming that a screen name is a network state.

# 3. Workflow Design Principles

WF-P01 — Engineering answer keys remain external to execution

Formal expected results come from approved test definitions and the Network Model. The current execution records observations and compares them; it cannot rewrite the expected result to match what occurred.

WF-P02 — Availability precedes execution

Every command is checked against the current mode, workflow stage, run identity, network state and engineering gate before any state change occurs. An unavailable command returns a traceable reason and creates no partial state change.

WF-P03 — Each state-changing action is one deterministic transaction

An accepted action updates the controlled scenario or observed state, records the initiating event, recalculates topology and source attribution, recalculates outage/customer impact, invalidates any superseded assessment, appends consequence events and only then exposes the completed revision.

WF-P04 — Isolation is proved by topology

Opening the named isolation switches is necessary in the formal baseline but is not itself accepted as proof. The derived active graph must show no available source path into SEC-A2 before BRK-A reclose or alternate restoration can proceed.

WF-P05 — Restoration permission is current-state bound

PERMITTED is evidence for one candidate at one run, configuration, telemetry snapshot and state revision. Any relevant change invalidates the assessment before another restoration command can be accepted.

WF-P06 — Information insufficiency takes precedence

Where a required point is missing, stale, UNCERTAIN, BAD or otherwise invalid, the assessment is BLOCKED. REJECTED is used only when required information is trustworthy and at least one engineering criterion fails. PERMITTED requires every criterion to pass.

WF-P07 — Formal and exploratory evidence do not mix

Formal Mode uses approved test definitions and produces FORMAL validation evidence. Exploration Mode uses reviewer-selected transient fault state and produces EXPLORATORY records that cannot satisfy a formal test without separate definition and execution.

WF-P08 — Operational history and engineering judgement remain distinct

Operational events reconstruct what the simulated environment did. Test conclusions, defects, corrections and review outcomes are separate engineering records linked to relevant event and evidence identifiers.

WF-P09 — Reset restores run state, not history

Reset creates a clean operational run from controlled initial conditions. It shall not delete configuration versions, completed validation executions, evidence snapshots, defect records or correction records.

WF-P10 — The defect is discoverable, not announced

The normal operational workflow exposes consequences and supporting data without highlighting the incorrect v1.0 endpoint as an answer. Configuration inspection is available during investigation, and the conclusion is recorded only after the engineer traces evidence to root cause.

# 4. Actors and Responsibilities

| Actor / function | Primary workflow responsibility | Shall not do |
| --- | --- | --- |
| Graduate Engineer | Select approved formal tests; verify initial conditions; execute or supervise defined steps; compare expected and observed results; investigate failures; document DEF-001; prepare correction and repeat-validation evidence. | Alter expected results during execution; infer PASS without evidence; delete failed results; change code to force a result. |
| Simulated Operator / Reviewer | Initiate defined simulated actions, acknowledge alarms, request assessment, execute a current permitted restoration and explore supported fault locations. | Bypass command gates; override topology or permissives; control real equipment. |
| Scenario Control | Create run context, enforce mode and action availability, advance controlled time, coordinate transactions and reset runs. | Calculate topology, outage, capacity or PASS/FAIL. |
| SCADA / Telemetry | Maintain observed values, quality and timestamps; derive alarm state from monitored change; record acknowledgement. | Own persistent connectivity or decide section energisation. |
| ADMS Topology | Derive active graph, source attribution, section energisation, radiality and isolation from configuration plus observed state. | Use canned section outcomes or treat fault status as energisation. |
| ADMS Restoration | Discover candidates; identify required evidence; evaluate permissives and capacity; issue NO_CANDIDATE, BLOCKED, REJECTED or PERMITTED. | Execute switching autonomously or keep permission after its evidence becomes stale. |
| OMS | Derive outage zones, affected customers and restored-customer deltas from current de-energised sections and customer mappings. | Infer outage directly from the fault label or expected answer. |
| Event / Audit | Append typed operational events in controlled chronological order. | Store engineering PASS/FAIL as an operational event or overwrite prior events. |
| Validation / Evidence | Bind approved tests to executions, capture immutable evidence, compare expected/observed, record PASS/FAIL and link defects/corrections/repeats. | Change operational state or treat a mutable screen as completed evidence. |
| Workspace | Present separate configuration, observed, derived, event and validation information; expose only currently available actions. | Calculate or override engineering results. |

The graduate engineer and simulated operator/reviewer may be represented by the same person during a recorded demonstration. Their conceptual responsibilities remain distinct so the work package shows both simulated operational action and independent engineering validation judgement.

# 5. Workflow Context, Identity and Lifecycle

## 5.1 Run Context

| Field | Workflow rule |
| --- | --- |
| scenario_run_id | Unique for every initialised or reset run. Never reused by a completed formal execution. |
| mode | FORMAL or EXPLORATION; fixed after initialisation. |
| configuration_version | Approved version selected by the test or exploration baseline; fixed for the run. |
| fault_section_id | SEC-A2 from the formal test; reviewer-selected represented section in Exploration Mode. |
| fault_type | Fixed abstract distribution-section fault causing affected-feeder protection operation. |
| scenario_time | Controlled clock used for timestamps, ordering and telemetry age. |
| state_revision | Monotonic revision incremented after every relevant scenario, device, telemetry or configuration-state transaction. |
| workflow_stage | Run progress descriptor separate from network state. |
| network_state_label | N0–N5 only where the formal state answer key is applicable; otherwise a derived scenario state. |
| evidence_class | FORMAL or EXPLORATORY; derived from mode, not user-editable during the run. |
| application_build_id | Recorded for validation reproducibility and proof that no code changed between comparative topology tests. |

## 5.2 Run and Validation Lifecycle

| Lifecycle state | Meaning | Permitted progression |
| --- | --- | --- |
| NOT_INITIALISED | No active run context. | Initialise a formal test or Exploration Mode run. |
| INITIALISED | Controlled configuration and initial state loaded; initial derivations complete. | Verify initial conditions; begin scenario. |
| ACTIVE | At least one accepted scenario action has occurred. | Continue available commands, capture checkpoints or reset. |
| ASSESSMENT_AVAILABLE | A current restoration assessment exists for the active revision. | Execute only if PERMITTED; otherwise change conditions or retain result. |
| RUN_COMPLETE | Defined scenario endpoint or test step set reached. | Complete formal comparison/evidence or reset for a new run. |
| EXECUTION_COMPLETED | Formal expected/observed comparison and PASS/FAIL are immutable. | Review, link defect/correction/repeat or start another execution. |

## 5.3 Record Identities and Links

| Record | Minimum links |
| --- | --- |
| Operational event | event ID → run ID → source/type/entity/state revision. |
| Restoration assessment | assessment ID → run/configuration/candidate/state revision/telemetry snapshot. |
| Evidence snapshot | evidence ID → run/state revision/content type/source record IDs/hash or immutable payload. |
| Validation execution | execution ID → test definition/run/configuration/build/expected/observed/evidence/PASS or FAIL. |
| Defect record | DEF-001 → failed execution/v1.0/root cause/engineering effect. |
| Correction record | correction ID → DEF-001/v1.0 approved endpoint change/v1.1/reviewer/date. |
| Repeat execution | new execution ID → original failed execution/DEF-001/correction/v1.1 evidence. |

# 6. Controlled Scenario Time and Telemetry Validity

## 6.1 Controlled Parameter PAR-TEL-001

| Parameter | Controlled value | Boundary rule | Purpose |
| --- | --- | --- | --- |
| PAR-TEL-001 — Maximum telemetry age | 60 seconds | Age ≤ 60.000 s is fresh; age > 60.000 s is stale. | Repeatable V1 restoration-validation threshold for the fictional demonstrator. |

The value resolves the parameter deferred by REQ-TEL-006 and the System Architecture. It is a project-specific validation constant, not a recommended setting for a real utility. Changing it after the validation baseline is established requires controlled engineering review because it affects telemetry boundary tests and restoration outcomes.

## 6.2 Age and Validity Rules

For each required monitored point, telemetry age is calculated using the controlled scenario clock:

Age = scenario_time − last_update_timestamp

- age from 0.000 through 60.000 seconds inclusive is FRESH;

- age greater than 60.000 seconds is STALE;

- a last-update timestamp later than the scenario time is INVALID_TIMESTAMP and insufficient evidence;

- quality GOOD and FRESH are both required for VALID operational telemetry;

- GOOD but STALE is invalid; UNCERTAIN or BAD is invalid regardless of age; and

- a telemetry value, quality or timestamp change increments the run state revision and invalidates a prior restoration assessment where the point is relevant.

## 6.3 Formal Restoration Evidence Set

For the formal SEC-A2 N4 assessment, the required monitored device set is BRK-A, BRK-B, SW-A12, SW-A23, SW-A34, SW-B12, SW-B23, SW-B34 and TS-01. Their combined states establish isolation, source availability, the candidate path and the absence of an unintended loop. Exploration Mode derives its required set from the selected fault, candidate path, isolation boundaries and radiality proof; it shall not assume that FDR-A is always affected or that FDR-B is always alternate.

# 7. Final Operational Event Catalogue

The following catalogue resolves the event subtype set deferred by the System Architecture. Every operational event includes event ID, controlled timestamp, source, type, run ID, state revision, affected entity where applicable, description, actor/origin where applicable and prior/new value where applicable.

| Event type | Source | Created when |
| --- | --- | --- |
| SCENARIO_INITIALISED | Scenario Control | A new run context and controlled initial state are created. |
| CONFIGURATION_SELECTED | Scenario Control / GIS | The run binds to v1.0 or v1.1 before scenario processing. |
| FAULT_INITIATED | Scenario Control | The abstract section fault becomes active. |
| TELEMETRY_UPDATED | SCADA / Telemetry | A monitored value, quality or timestamp changes. |
| DEVICE_STATE_CHANGE | SCADA / Telemetry | Observed breaker or switch value changes, with previous/new values. |
| ALARM_GENERATED | SCADA / Telemetry | The feeder-trip condition creates the defined alarm. |
| ALARM_ACKNOWLEDGED | Operator / SCADA | An active unacknowledged alarm is acknowledged. |
| SWITCHING_ACTION | Operator / Scenario Control | An authorised simulated isolation or restoration operation is accepted. |
| TOPOLOGY_RECALCULATED | ADMS Topology | A completed revision derives graph, sources, energisation and radiality. |
| OUTAGE_UPDATED | OMS | The affected section/zone set or customer total is recalculated, including no-change results where required for traceability. |
| RESTORATION_CANDIDATE_IDENTIFIED | ADMS Restoration | One traceable candidate is selected for assessment. |
| RESTORATION_NO_CANDIDATE | ADMS Restoration | Generic discovery finds no eligible candidate under current conditions. |
| RESTORATION_ASSESSED | ADMS Restoration | A candidate receives BLOCKED, REJECTED or PERMITTED with reasons and evidence. |
| RESTORATION_ASSESSMENT_INVALIDATED | ADMS Restoration | A relevant change supersedes a prior assessment. |
| SCENARIO_RESET | Scenario Control | The active run is closed/reset and a clean run is requested. |

Validation execution creation, evidence capture, PASS/FAIL, DEF-001 recording, correction approval and review are engineering records rather than operational event subtypes. They reference the operational history but do not appear as though they were utility operating events.

# 8. Common Command and Transaction Rules

## 8.1 Command Envelope

Every requested command carries the actor, run ID, expected current state revision, command type, target entity where applicable and controlled request time. State-changing commands use optimistic revision matching: if the requested revision is not current, the command is unavailable and the user must review the latest state before retrying. This prevents a command authorised against stale presentation state from changing the run.

## 8.2 Precondition and Outcome

| Command | Minimum availability gate | Accepted outcome |
| --- | --- | --- |
| INITIALISE_RUN | No active mutable run; valid mode; approved configuration; formal test selected or valid exploration section selected. | Create run, bind context, load controlled states, derive N0/current initial state and append initial events. |
| INITIATE_FAULT | Run INITIALISED/ACTIVE; no active fault; target matches mode rule; initiating protection consequence defined. | Set fault state; update affected feeder breaker telemetry to OPEN; alarm/recalculate/outage transaction. |
| ACKNOWLEDGE_ALARM | Matching alarm is active and unacknowledged. | Change acknowledgement state and append event; no topology revision. |
| OPERATE_ISOLATION_DEVICE | Target is an authorised simulated device and requested state is allowed in the current workflow. | Append switching action; update device telemetry; recalculate and invalidate old assessment. |
| RESTORE_NORMAL_SOURCE | Fault isolation is proved by current topology and target healthy section cannot be connected to fault. | Apply authorised breaker operation, recalculate and expose restored section/customer delta. |
| ASSESS_RESTORATION | Current topology/outage transaction complete; no state-changing command pending. | Discover candidate or record no candidate; if candidate exists, capture evidence and issue BLOCKED/REJECTED/PERMITTED. |
| EXECUTE_RESTORATION | Current PERMITTED assessment matches run/configuration/candidate/state revision and has not expired or been invalidated. | Apply only candidate-defined simulated switching, recalculate and record results. |
| CAPTURE_FORMAL_CHECKPOINT | Formal execution active; required workflow checkpoint reached. | Create immutable evidence references without changing operational state. |
| RESET_RUN | An active run exists. | Close current mutable run state and create/prepare a clean run without deleting history. |

## 8.3 State-Changing Transaction Order

- validate command availability and expected state revision;

- advance controlled scenario time where the workflow step defines an increment;

- apply the single authorised scenario, observed-device or telemetry change;

- append the initiating operational event or events;

- increment state_revision;

- derive active topology, source paths, section energisation, fault isolation and radiality;

- derive outage sections, customer zones, affected total and restored-customer delta;

- invalidate any restoration assessment bound to an earlier relevant revision;

- append topology, outage and invalidation events in deterministic order; and

- publish the complete new revision for presentation and optional evidence capture.

The transaction is atomic from the user’s perspective. A failure before completion leaves the prior revision unchanged and returns an engineering-readable reason. V1 does not need distributed messaging or partial-event recovery because it is one local controlled demonstrator.

## 8.4 Assessment-Only Transaction

ASSESS_RESTORATION does not change device state or increment the electrical topology revision. It reads one completed revision, performs candidate discovery, captures the required telemetry/topology/load evidence, evaluates decision precedence, creates an immutable assessment and appends candidate/assessment events. The formal workflow may label the resulting engineering decision state N4 while retaining the N3 physical topology and state revision.

# 9. Formal Validation Initialisation — WF-FML-001

Formal Mode begins from an approved version-controlled test definition. The definition supplies its test ID, requirement links, objective, configuration version, initial conditions, step sequence and expected result. The operator/reviewer may select an approved test but cannot edit those fields inside the execution.

| Step | Actor / function | Action and required result | Evidence |
| --- | --- | --- | --- |
| FML-01 | Graduate Engineer | Select the approved formal test definition. Confirm the test names SEC-A2 where the controlled scenario requires it. | Test definition ID/version and requirement links. |
| FML-02 | Scenario Control | Bind mode FORMAL, test-specified configuration, SEC-A2, abstract fault type, controlled clock, FORMAL evidence class and build ID. | Run-context record. |
| FML-03 | GIS / SCADA | Load persistent configuration separately from controlled observed device values, qualities and timestamps. | Configuration identity and initial telemetry snapshot. |
| FML-04 | ADMS / OMS | Derive initial topology, source attribution, energisation, outage and customer result using normal processing. | Initial derived-state and calculation snapshot. |
| FML-05 | Graduate Engineer | Compare actual initial conditions with the test definition. If any mismatch exists, do not start; correct/reset the initialisation issue. | Initial-condition check result. |
| FML-06 | Validation / Evidence | Create a new execution identity linked to the run. Preserve expected results before the first scenario action. | Execution record with status RUNNING. |

# 10. Formal SEC-A2 Network Workflow — N0 to N5

This sequence is the exact workflow expression of Network Model Section 16. It uses corrected Network Configuration v1.1 for the intended baseline. Alarm acknowledgement and evidence capture are workflow actions within the sequence but do not create new engineering network states. Each individual switch operation recalculates the network before the next action is considered.

Figure 1 — Formal SEC-A2 operator/system/validation workflow and N0–N5 gates

## 10.1 N0 — Controlled Normal State

| Condition | Required N0 value |
| --- | --- |
| Configuration | Corrected v1.1; intended SW-A23 endpoint SEC-A2 ↔ SW-A23 ↔ SEC-A3. |
| Device state | BRK-A/BRK-B and all sectionalising switches CLOSED; TS-01 OPEN. |
| Fault/alarm | No active fault; no feeder-trip alarm. |
| Source attribution | SEC-A1–SEC-A4 from FDR-A; SEC-B1–SEC-B4 from FDR-B. |
| Energisation/outage | All sections ENERGISED; zero affected customers. |
| Telemetry | Required points GOOD and fresh under PAR-TEL-001. |
| Topology | Radial; exactly one active source path per section. |

The graduate engineer captures the N0 initial-condition evidence before fault initiation. If the run does not satisfy N0, the formal execution does not continue because later comparison would no longer use the approved initial conditions.

## 10.2 Transition N0 → N1 — Fault and Protection Operation

- the operator/reviewer requests INITIATE_FAULT for the test-defined SEC-A2;

- Scenario Control marks SEC-A2 FAULTED and appends FAULT_INITIATED;

- SCADA updates BRK-A from CLOSED to OPEN with quality GOOD and a current controlled timestamp;

- SCADA appends TELEMETRY_UPDATED, DEVICE_STATE_CHANGE and ALARM_GENERATED for the feeder trip;

- ADMS recalculates using unchanged v1.1 connectivity and the new breaker state;

- OMS recalculates from the derived de-energised section set; and

- the completed revision becomes N1 and may be captured as formal evidence.

## 10.3 N1 — Post-Fault / Feeder Trip

| Item | Expected N1 result |
| --- | --- |
| Observed state | BRK-A OPEN; BRK-B CLOSED; sectionalising switches CLOSED; TS-01 OPEN. |
| Fault status | SEC-A2 FAULTED; fault status remains independent from energisation. |
| Energisation | SEC-A1–SEC-A4 DE-ENERGISED; SEC-B1–SEC-B4 ENERGISED. |
| Affected customers | 850 = 180 + 220 + 260 + 190. |
| Alarm | Feeder A trip alarm ACTIVE and initially UNACKNOWLEDGED. |
| Restoration | No alternate restoration execution available before fault isolation. |

## 10.4 Alarm Acknowledgement Within N1

The operator/reviewer acknowledges the active Feeder A trip alarm. The system records the actor, alarm ID and controlled time, changes the acknowledgement state and appends ALARM_ACKNOWLEDGED. The action does not change BRK-A, connectivity, section energisation, outage extent, affected customers or the N1 network-state label.

## 10.5 Transition N1 → N2 — Fault Isolation

The operator/reviewer opens SW-A12 and SW-A23 as two separate authorised simulated switching actions. After each accepted action the normal transaction sequence records the operation and device state, recalculates topology and outage, and invalidates any older assessment. The workflow does not batch both switches into an unexplained state jump.

- after SW-A12 opens, SEC-A2 remains connected downstream through SW-A23 but has no normal source because BRK-A is open; all Feeder A sections remain de-energised and 850 customers remain affected;

- after SW-A23 opens, the active graph is recalculated and must show no source path into SEC-A2 from either feeder; and

- only that derived isolation proof permits the workflow to label N2 and expose the BRK-A normal-source restoration action.

## 10.6 N2 — Fault Isolated

| Condition | Required N2 result |
| --- | --- |
| Isolation devices | SW-A12 OPEN and SW-A23 OPEN. |
| Faulted section | SEC-A2 FAULTED, DE-ENERGISED and without an active source path. |
| Other Feeder A sections | SEC-A1, SEC-A3 and SEC-A4 remain DE-ENERGISED while BRK-A and TS-01 are open. |
| Affected customers | 850. |
| Isolation permissive | PASS from topology proof, not from switch names alone. |

## 10.7 Transition N2 → N3 — Restore SEC-A1 from FDR-A

The operator/reviewer requests BRK-A closure only after the current derived topology proves SEC-A2 isolation. The accepted simulated switching action changes BRK-A OPEN → CLOSED and triggers normal recalculation. SW-A12 prevents the healthy upstream source from reaching SEC-A2; SW-A23 separates the downstream restoration zone from the fault.

## 10.8 N3 — Healthy Upstream Section Restored

| Item | Expected N3 result |
| --- | --- |
| Source attribution | SEC-A1 supplied from FDR-A; SEC-A2/A3/A4 have no active source. |
| Energisation | SEC-A1 ENERGISED; SEC-A2/A3/A4 DE-ENERGISED. |
| Affected customers | 670 = 220 + 260 + 190; 180 restored at this transition. |
| Fault status | SEC-A2 remains FAULTED. |
| Tie state | TS-01 remains OPEN. |

## 10.9 Transition N3 → N4 — Restoration Assessment

The operator/reviewer requests ASSESS_RESTORATION. Candidate discovery identifies healthy de-energised SEC-A3 and SEC-A4 as a transferable group with the alternate path through TS-01 from FDR-B. The system captures the candidate, source path, fault-isolation proof, radiality result, required telemetry, loads and calculation basis before deciding the outcome.

## 10.10 N4 — Candidate Assessed and PERMITTED

| Decision element | Formal result |
| --- | --- |
| Candidate | Restore SEC-A3 and SEC-A4 by closing TS-01 from FDR-B. |
| Fault isolation | PASS — SW-A12 and SW-A23 open; SEC-A2 excluded from active source paths. |
| Alternate source | PASS — BRK-B CLOSED and FDR-B available. |
| Radial topology | PASS — candidate produces no unintended loop. |
| Telemetry validity | PASS — all nine required points GOOD and age ≤ 60.000 s. |
| Transferable load | 1.50 MW = 0.85 + 0.65 MW. |
| Resulting FDR-B load | 5.70 MW = 4.20 + 1.50 MW. |
| Loading/capacity | 95.0% = 5.70 / 6.00 × 100; PASS. |
| Assessment | PERMITTED and bound to the active run, v1.1, candidate, telemetry snapshot and current state revision. |
| Physical topology | Unchanged from N3; TS-01 remains OPEN. |

## 10.11 Transition N4 → N5 — Authorised Tie Closure

The operator/reviewer deliberately requests EXECUTE_RESTORATION against the current assessment ID. Scenario Control revalidates the run, configuration, candidate and state revision. If they still match and the result remains PERMITTED, TS-01 changes OPEN → CLOSED as a simulated switching action. Any mismatch, intervening telemetry change or invalidation makes the action unavailable and requires reassessment.

## 10.12 N5 — Healthy Downstream Sections Restored

| Item | Expected N5 result |
| --- | --- |
| Device state | BRK-A/BRK-B CLOSED; SW-A12/SW-A23 OPEN; SW-A34 and B sectionalising switches CLOSED; TS-01 CLOSED. |
| Source attribution | SEC-A1 from FDR-A; SEC-A3/A4 from FDR-B; SEC-A2 no source. |
| Energisation | SEC-A1/A3/A4 and all B sections ENERGISED; SEC-A2 DE-ENERGISED and FAULTED. |
| Affected/restored customers | 220 remain affected on SEC-A2; 450 restored through FDR-B; 180 previously restored through FDR-A. |
| Loading | FDR-B 5.70 MW / 95.0%; FDR-A supplies SEC-A1 only. |
| Topology | Radial; open isolation boundaries prevent the alternate path reaching the fault or FDR-A source. |

# 11. Restoration Outcome and Invalidation Workflows

## 11.1 Decision Precedence

| Order | Condition | Workflow result | Execution availability |
| --- | --- | --- | --- |
| 1 | No healthy de-energised restorable group/path can be formed. | NO_CANDIDATE; record reason and current topology. | Unavailable. |
| 2 | Candidate exists but any required value/quality/timestamp is missing, stale, UNCERTAIN, BAD or invalid. | BLOCKED; identify every insufficient evidence item. | Unavailable. |
| 3 | Required information is trustworthy but fault isolation, alternate source, radiality or capacity fails. | REJECTED; identify each failed criterion and calculation. | Unavailable. |
| 4 | Candidate exists, required evidence is valid and every engineering criterion passes. | PERMITTED; bind to current candidate and revision. | Available only while binding remains current. |

BLOCKED precedence avoids presenting a definitive engineering rejection when the system lacks reliable evidence. Known criteria may still be displayed for learning, but the final result and primary reason remain BLOCKED until the evidence problem is resolved.

## 11.2 Assessment Invalidation

A current restoration assessment is invalidated when any change could alter its evidence or conclusion. Relevant changes include device value, quality or timestamp; scenario time sufficient to cross PAR-TEL-001; fault identity/state; source availability; configuration version; candidate definition; topology state; load/capacity input; or run reset. Invalidation appends RESTORATION_ASSESSMENT_INVALIDATED with the superseding revision/reason and removes restoration execution availability. The assessment record itself remains preserved.

## 11.3 No Manual Override

V1 provides no override that converts NO_CANDIDATE, BLOCKED or REJECTED to PERMITTED. The user may correct a controlled input where the current workflow allows it, then request a new assessment. The new result receives a new assessment ID and evidence snapshot.

# 12. Stale-Telemetry Negative Workflow — WF-NEG-001

The stale-telemetry case is a separate negative functional validation case, not DEF-001. Correct system behaviour is an operational BLOCKED outcome and an engineering test PASS where the approved expected result is BLOCKED.

| Step | Action | Expected result / evidence |
| --- | --- | --- |
| NEG-01 | Initialise the approved negative test using corrected v1.1 and reach the controlled pre-assessment state equivalent to N3. | Fault isolated; SEC-A1 restored; candidate conditions otherwise available. |
| NEG-02 | Set TS-01 value OPEN and quality GOOD, but establish last_update_timestamp so age is 60.001 s at assessment time. | Value and quality appear acceptable; freshness is STALE by PAR-TEL-001. |
| NEG-03 | Request restoration assessment. | Candidate identified; required telemetry list includes TS-01. |
| NEG-04 | Evaluate validity before engineering rejection criteria. | Final operational outcome BLOCKED; reason identifies TS-01 stale age 60.001 s > 60.000 s. |
| NEG-05 | Attempt to execute restoration. | Command unavailable; TS-01 remains OPEN; no switching action is accepted. |
| NEG-06 | Capture expected/observed and complete test. | Observed BLOCKED matches expected BLOCKED; engineering result PASS. |

Boundary validation shall also cover exactly 60.000 seconds as FRESH and a future-dated timestamp as invalid evidence. UNCERTAIN and BAD quality cases follow the same blocking workflow with their own expected reasons; freshness and quality remain independent.

# 13. Exploration Mode Workflow — WF-EXP-001

Exploration Mode is a reviewer-driven demonstration path that uses the same Network Configuration v1.1 and the same generic topology, outage and restoration logic as formal validation. It does not modify the formal SEC-A2 baseline or create formal validation evidence.

| Step | Actor / function | Workflow rule |
| --- | --- | --- |
| EXP-01 | Reviewer | Select EXPLORATION and one represented section: SEC-A1–SEC-A4 or SEC-B1–SEC-B4. |
| EXP-02 | Scenario Control | Bind corrected v1.1, selected fault section as transient scenario state, fixed abstract fault type and EXPLORATORY evidence class. |
| EXP-03 | System | Derive the selected section’s feeder and protection consequence from configuration; do not assume FDR-A/FDR-B roles. |
| EXP-04 | Reviewer | Initiate the fault and use only actions made available by generic state and topology rules. |
| EXP-05 | ADMS / OMS | Derive source attribution, de-energised sections, affected customers and restoration opportunity after every operation. |
| EXP-06 | ADMS Restoration | Return no candidate, BLOCKED, REJECTED or PERMITTED according to actual topology, telemetry and capacity. |
| EXP-07 | Workspace / Evidence | Display mode, selected section and EXPLORATORY classification throughout; retain records separately from formal executions. |

## 13.1 Feeder-Role Reversal

Where a Feeder B section is selected, FDR-B becomes the affected feeder and any available alternate supply is derived from FDR-A. The interface and logic shall use derived affected_feeder_id and alternate_feeder_id rather than labels that imply Feeder A is always faulted. Candidate load and capacity are calculated from the selected healthy section group and actual alternate-feeder conditions.

## 13.2 Exploration Outcome Boundary

Exploration is not required to reproduce N0–N5 or to find a restorable group for every section. A fault near a source, unavailable isolation boundary, insufficient alternate capacity, invalid telemetry or topology constraint may legitimately prevent restoration. The educational value is the traceable engineering reason, not forced success.

## 13.3 Conversion to Formal Validation

An exploration result cannot be relabelled FORMAL. If a case is worth validating, a new controlled test definition must specify its ID, requirements, objective, configuration, initial conditions, steps and expected result before a separate formal execution begins.

# 14. Formal Validation Execution and Evidence Workflow

## 14.1 Test Definition Versus Execution

| Approved test definition | Immutable execution record |
| --- | --- |
| Test ID and definition version | Unique validation_execution_id |
| Requirement links and objective | Referenced unchanged from definition |
| Required configuration and initial conditions | Actual configuration, build, run and initial-condition check |
| Defined steps/checkpoints | Completed steps and associated event/evidence IDs |
| Expected engineering result defined before execution | Observed result captured from immutable state revisions |
| Acceptance comparison rule | PASS/FAIL plus reason and evidence references |

## 14.2 Checkpoint Capture

At each test-defined checkpoint, Validation/Evidence captures or references the exact configuration identity, run context, state revision, telemetry snapshot, derived topology/source attribution, energisation, outage/customer calculation, restoration assessment and relevant operational events. Evidence capture does not change the scenario. A later screen state cannot replace or modify what the checkpoint recorded.

## 14.3 Completion and Determination

- confirm every required test step and checkpoint is complete;

- derive the observed result only from captured run evidence;

- compare the observed result with the pre-existing expected result;

- record PASS when they agree, including expected safety blocking; otherwise record FAIL;

- record concise comparison reasons and requirement links;

- freeze the completed execution and its evidence links; and

- route a failed seeded-defect execution to the DEF-001 investigation workflow without deleting or reopening it.

# 15. Seeded-Defect Execution — WF-DEF-001

VT-TOP-DEF-001 deliberately uses Network Configuration v1.0 while keeping the SEC-A2 fault input, initiating telemetry, algorithms and expected engineering answer unchanged. The test ends at the immediate post-trip state corresponding to N1 so the incorrect topology consequence is isolated and reviewable.

| Element | Expected engineering baseline | Observed with v1.0 |
| --- | --- | --- |
| SW-A23 relationship | SEC-A2 ↔ SW-A23 ↔ SEC-A3 | SEC-B3 ↔ SW-A23 ↔ SEC-A3 |
| Initiating telemetry | BRK-A OPEN, GOOD and fresh | BRK-A OPEN, GOOD and fresh — correct |
| SEC-A1 / SEC-A2 | DE-ENERGISED | DE-ENERGISED |
| SEC-A3 / SEC-A4 | DE-ENERGISED after loss of FDR-A source | Incorrectly ENERGISED from FDR-B through SEC-B3 and SW-A23 |
| Affected customers | 850 on A1–A4 | 400 on A1/A2 only |
| Difference | None | 450 customers understated: CZ-A3 260 + CZ-A4 190 |
| Test result | Observed shall match expected 850-customer outage | FAIL |

The topology engine and OMS are functioning according to their configured inputs: the wrong configuration is processed normally and its downstream consequences are exposed. The workflow prohibits defect-specific application branches, hard-coded 400-customer results or altered expected values.

# 16. Defect Investigation Workflow

Figure 2 — Controlled path from failed v1.0 execution through DEF-001, v1.1 correction and regression

| Step | Engineer investigation activity | Required finding/evidence |
| --- | --- | --- |
| INV-01 | Preserve and review the completed VT-TOP-DEF-001 FAIL. | Expected 850, observed 400, exact execution/run/configuration/build identities. |
| INV-02 | Verify initiating SCADA evidence. | BRK-A is OPEN, GOOD and fresh; telemetry error is ruled out. |
| INV-03 | Compare expected and observed energisation/source attribution by section. | A3/A4 are unexpectedly energised from FDR-B while A1/A2 are de-energised. |
| INV-04 | Verify OMS inputs and customer-zone arithmetic. | OMS correctly sums the observed de-energised set A1/A2: 180 + 220 = 400. |
| INV-05 | Trace the unexpected active source path from SEC-A3 toward FDR-B. | Path passes SEC-A3 → SW-A23 → SEC-B3 and the healthy Feeder B graph. |
| INV-06 | Inspect v1.0 configured endpoints and compare them with the Network Model. | SW-A23 endpoint 1 is SEC-B3 instead of intended SEC-A2; endpoint 2 remains SEC-A3. |
| INV-07 | Record root cause and engineering propagation. | DEF-001 links incorrect connectivity → incorrect energisation → incorrect outage set → 450-customer understatement. |

The investigation path works from consequence to source. The normal operational view does not reveal the endpoint as the answer before investigation, but the engineer can inspect source paths, configuration relationships and evidence once the failure is being analysed.

# 17. Correction and Repeat Validation — WF-COR-001

## 17.1 Controlled Correction

| Correction item | Required record |
| --- | --- |
| Defective version | Preserve Network Configuration v1.0 and its exact endpoint relationship. |
| Approved change | Change SW-A23 endpoint 1 from SEC-B3 to SEC-A2; endpoint 2 remains SEC-A3. |
| Corrected version | Create separately identifiable Network Configuration v1.1. |
| Unchanged items | Assets, identifiers, loads, customers, normal states, telemetry, algorithms, test definition and expected result. |
| Engineering effect | Removes unintended FDR-B source path into SEC-A3/A4 and restores intended Feeder A topology. |
| Traceability | Correction record links DEF-001, v1.0, approved endpoint change, v1.1 and reviewer/date. |

## 17.2 Direct Repeat of VT-TOP-DEF-001

- start a new formal execution using the same approved test definition and expected result;

- bind corrected v1.1 and record the application build ID; no topology, OMS or validation code change is allowed between comparative tests;

- recreate the same controlled N0 conditions and SEC-A2 initiating fault;

- observe BRK-A OPEN with GOOD, fresh telemetry;

- confirm SEC-A1–SEC-A4 are DE-ENERGISED and affected customers equal 850;

- record PASS as a new immutable execution linked to the original FAIL, DEF-001 and correction record; and

- retain the original failed execution and v1.0 unchanged.

## 17.3 Full N0–N5 Regression

After the direct repeat passes, execute the complete formal v1.1 N0–N5 workflow. The regression confirms normal source attribution, 850-customer trip consequence, topology-proved isolation, SEC-A1 normal-source restoration, N4 candidate and 5.70 MW / 95.0% PERMITTED assessment, N5 alternate restoration of 450 customers and the final 220-customer outage. DEF-001 is resolved only when the direct repeat passes; the regression additionally confirms that the correction did not disturb the wider controlled scenario.

# 18. Reset and Repeat Semantics

| Reset effect | Required behaviour |
| --- | --- |
| Run identity | Close/reference the prior run and assign a new scenario_run_id for the clean repeat. |
| Configuration | Reload the version required by the selected test or exploration baseline; never rewrite v1.0/v1.1. |
| Observed state | Restore defined normal breaker/switch values, GOOD quality and controlled initial timestamps. |
| Scenario/derived state | Clear active fault and alarm; recalculate normal topology, energisation and zero outage. |
| Assessment | Remove current availability; preserve prior assessment record and invalidation history. |
| Operational events | Prior run remains append-only; new run starts its own chronological history. |
| Formal evidence | Completed executions and snapshots remain immutable and linked to their original run. |

Reset is available from an active or completed run but is not an undo operation. If a user needs to inspect an earlier result, the workspace reads the preserved run/evidence rather than reconstructing it by changing the current mutable state.

# 19. Evidence Assembly and Engineering Review — WF-EVD-001

## 19.1 Minimum Formal Evidence Package

- project/test identity, test-definition version, requirement links and objective;

- execution, run, mode, configuration and application-build identities;

- controlled initial conditions and scenario clock basis;

- expected result fixed before execution;

- telemetry values, qualities, timestamps, calculated ages and freshness classification;

- topology/source-path, section-energisation and fault-state snapshots;

- outage section/customer-zone set and customer arithmetic;

- restoration candidate, required telemetry set, every permissive, load/capacity calculation and result;

- chronological operational event references;

- observed result, PASS/FAIL and comparison reason;

- for defect work: original FAIL, DEF-001, configuration endpoint evidence, correction record, v1.1 repeat PASS and regression result; and

- review status, reviewer comments and preparation/review dates without implying production commissioning approval.

## 19.2 Assembly Rules

Evidence assembly reads preserved records and does not modify them. A reviewable package may contain human-readable summaries and diagrams, but every conclusion must retain stable IDs and links back to the immutable source evidence. A screenshot alone is insufficient where the underlying state can change or where identifiers/calculation inputs are not visible.

## 19.3 Review Sequence

| Review step | Reviewer question |
| --- | --- |
| Completeness | Are every required test step, checkpoint, requirement link and evidence category present? |
| Reproducibility | Can the run be repeated from recorded configuration, initial conditions, scenario time and build identity? |
| Engineering correctness | Do expected/observed, topology, outage and restoration calculations agree with the approved baseline? |
| Traceability | Can each conclusion be followed to configuration, telemetry, event and evidence records? |
| Change control | Are v1.0/v1.1, DEF-001 and correction relationships preserved without overwrite? |
| Presentation | Is the package clearly fictional/simulated and understandable to an OT engineering reviewer? |

# 20. Command Availability by Formal Network State

| Action | N0 | N1 | N2 | N3 | N4 | N5 |
| --- | --- | --- | --- | --- | --- | --- |
| Initiate SEC-A2 fault | Available | No | No | No | No | No |
| Acknowledge trip alarm | No | If active/unack. | If still unack. | If still unack. | If still unack. | If still unack. |
| Open SW-A12 / SW-A23 | No | Available in sequence | Already open | Already open | Already open | Already open |
| Close BRK-A | Already closed | No — fault not isolated | Available after proof | Already closed | Already closed | Already closed |
| Assess alternate restoration | No | No | No — complete N2 → N3 first | Available | Reassess if invalidated | Not required |
| Close TS-01 | No | No | No | No | Only with current PERMITTED | Already closed |
| Capture formal checkpoint | As defined | As defined | As defined | As defined | As defined | As defined |
| Reset | Available | Available | Available | Available | Available | Available |

The matrix describes the controlled baseline, not a universal power-system switching procedure. The implementation shall calculate availability from workflow rules and current derived state; it shall not permit a user to jump directly to a desired N-state.

# 21. Invalid Action Handling

| Failure class | Required response |
| --- | --- |
| Unavailable workflow action | Reject before mutation; state unchanged; explain required prior condition. |
| Stale command revision | Reject before mutation; identify requested/current revisions; require refresh/review. |
| Invalid mode input | Reject; formal fault/test inputs cannot be edited and exploration must select a represented section. |
| Isolation not proved | Do not expose/accept source reclose or restoration execution; show derived source-path reason. |
| Assessment not current | Reject execution; link invalidated assessment and require new assessment. |
| Missing/unreliable assessment evidence | Complete assessment as BLOCKED where a candidate exists; list each evidence deficiency. |
| Engineering criterion failure | Complete assessment as REJECTED with criterion/calculation evidence. |
| Processing error before transaction completion | Retain prior state revision; record a diagnostic engineering error separately from normal operational events. |

# 22. Workflow Information Handoffs

| From → to | Workflow payload | Contract |
| --- | --- | --- |
| Scenario Control → SCADA / Topology | Accepted scenario/device/telemetry action plus run and expected revision. | One controlled mutation only. |
| GIS + SCADA → ADMS Topology | Configuration identity/connectivity plus observed states/quality/timestamps. | No duplicated or hard-coded source roles. |
| ADMS Topology → OMS | Revision, de-energised sections and source attribution. | OMS uses derived set, not fault label. |
| ADMS Topology/SCADA/GIS → Restoration | Candidate graph, isolation/radiality/source evidence, monitored-point validity, loads/capacities. | Assessment bound to exact revision/snapshot. |
| Operational functions → Event / Audit | Typed event content and run context. | Append-only chronological record. |
| Operational functions → Validation / Evidence | Immutable snapshots or stable record references. | Evidence capture does not mutate source state. |
| Validation → Workspace | Test definition, execution status, comparison and evidence links. | Presentation cannot alter expected result or judgement records. |

# 23. Requirements Allocation

The workflow design allocates all 124 unique formal requirements. Allocation identifies where behaviour is exercised or constrained; the System Architecture remains authoritative for principal component ownership and the Requirements Specification remains authoritative for exact wording and verification method.

| Workflow area | Requirement allocation |
| --- | --- |
| Run initialisation and network context | REQ-NET-001–011; REQ-NFR-002–004; REQ-NFR-009 |
| Topology and state-changing transaction | REQ-TOP-001–009; REQ-NFR-003; REQ-NFR-006 |
| Controlled time and telemetry validity | REQ-TEL-001–010 |
| Alarm generation and acknowledgement | REQ-ALM-001–005 |
| Outage/customer consequence | REQ-OUT-001–007 |
| Restoration discovery, assessment and execution | REQ-RST-001–029 |
| Operational event catalogue and history | REQ-EVT-001–011 |
| Formal execution, evidence, negative tests and reset | REQ-VAL-001–014 |
| Defect investigation, correction and repeat | REQ-CFG-001–012 |
| Exploration Mode | REQ-EXP-001–007 |
| Presentation/review boundaries | REQ-NFR-001; REQ-NFR-005; REQ-NFR-007–008 plus cross-functional clarity and reviewability obligations |

# 24. Workflow Decisions

| Decision ID | Workflow decision |
| --- | --- |
| AD-WF-001 | Treat workflow stage and N0–N5 engineering network state as separate information. |
| AD-WF-002 | Use a unique run identity after every initialisation/reset; reset never deletes preserved history. |
| AD-WF-003 | Fix PAR-TEL-001 at 60 seconds: age ≤ 60.000 s fresh; age > 60.000 s stale; future timestamps invalid. |
| AD-WF-004 | Use the final 15-type operational event catalogue in Section 7 and keep engineering records separate. |
| AD-WF-005 | Process every state-changing action as a deterministic atomic transaction with one published new revision. |
| AD-WF-006 | Perform SW-A12 and SW-A23 isolation as separate operations with recalculation after each. |
| AD-WF-007 | Permit BRK-A reclose only after current topology proves the active fault section has no source path. |
| AD-WF-008 | Represent N4 as an assessment-only engineering state; TS-01 remains OPEN and the topology revision is unchanged. |
| AD-WF-009 | Give BLOCKED precedence for insufficient evidence, then REJECTED for failed criteria, and PERMITTED only for all-pass. |
| AD-WF-010 | Bind restoration execution to the current assessment ID, run, configuration, candidate and state revision. |
| AD-WF-011 | Use corrected v1.1 as ordinary Exploration Mode baseline and derive feeder roles generically from selected fault/topology. |
| AD-WF-012 | Do not convert exploratory output into formal evidence; require a separately approved test and execution. |
| AD-WF-013 | Investigate DEF-001 from consequence to source without revealing the incorrect endpoint in the normal operational view. |
| AD-WF-014 | Record application build identity and make no code change between v1.0/v1.1 comparative topology tests. |
| AD-WF-015 | Preserve original FAIL, DEF-001, correction, repeat PASS and regression as separate linked records. |
| AD-WF-016 | Evidence assembly reads immutable sources and cannot reduce traceability to an unlinked screenshot. |
| AD-WF-017 | For the active fault, derive incident switchable boundaries from configuration, evaluate A/B/C evidence, expose only authorised OPEN actions and fully recalculate after every accepted command or valid telemetry update until all boundaries are proven OPEN and zero source paths remain. |

# 25. Controlled Deferred Items

The following implementation-facing choices remain intentionally deferred. They shall be resolved in their named stage before code relies on them; no developer shall guess them inside application logic.

| Item | Workflow constraint already established | Resolution stage |
| --- | --- | --- |
| Technology stack and module structure | Must preserve deterministic transactions and the nine logical ownership boundaries. | Step 8 — Demonstrator Design |
| Persistence and identifier format | Must preserve versions, immutable completed evidence, unique IDs and links. | Step 8 — Demonstrator Design |
| Detailed screen/navigation design | Must expose current mode/state/gates and separate configuration, observed, derived, event and validation information. | Step 8 — Demonstrator Design |
| Exact evidence export file/report format | Must remain reviewable, immutable and traceable to source records. | Demonstrator Design / Validation Plan |
| Complete formal test catalogue and test IDs beyond VT-TOP-DEF-001 | Must implement these workflows and all requirement verification methods without changing the answer key. | Validation Plan |
| Controlled per-step time increments | Must remain deterministic and satisfy PAR-TEL-001 boundary cases. | Validation Plan / test definitions |

# 26. Workflow Completion and Next Stage

Sections 1–25 establish the Step 7 Workflow Design for V1. They define actor responsibilities, controlled run identities, the 60-second telemetry threshold, final operational event catalogue, command/transaction gates, the formal SEC-A2 N0–N5 sequence, restoration result precedence, negative telemetry behaviour, Exploration Mode, validation evidence, DEF-001 investigation, v1.1 correction, repeat validation, regression and evidence review while allocating all 124 formal requirements.

The next lifecycle activity is Step 8 — Demonstrator Design. It shall translate these workflows and the System Architecture into a concrete local application design: module/API boundaries, persistent and run-scoped data structures, identifier formats, screen/view model, navigation, action availability presentation, evidence storage/export approach and implementation/test plan. Step 8 shall implement the approved engineering workflow rather than invent new operational decisions in code.

# 27. Controlled Amendment — DC-003 Generic Isolation Workflow

## 27.1 Entry and Derivation

| Sequence | Actor / component | Controlled activity | Required result / record |
| --- | --- | --- | --- |
| 1 | Scenario Coordinator | Receive the active fault section and current run/configuration revision. | Active fault remains transient scenario state; formal mode remains SEC-A2. |
| 2 | Topology Processing | Query the selected configuration for all directly incident switchable devices. | Complete boundary-device set returned from connectivity; no section lookup. |
| 3 | Telemetry + Topology | Evaluate each device value, quality, timestamp and freshness under Conditions A/B/C. | Each boundary becomes PROVEN OPEN, PROVEN CLOSED or UNPROVEN with evidence/reason. |
| 4 | Coordinator | Apply existing workflow, actor, revision and command gates to PROVEN CLOSED boundaries. | Zero, one or multiple authorised OPEN actions may be available; no CLOSE isolation action. |
| 5 | Operator/reviewer | Select at most one currently authorised OPEN action. | Accepted command is recorded before derived recalculation. |
| 6 | Coordinator + domain engine | Recalculate boundary status, available actions, topology, source paths, energisation, outage and proof. | All derived records bind to the new revision; stale prior actions are invalid. |
| 7 | Workflow gate | Repeat evidence correction or one-action execution as required. | Isolation is complete only when every boundary is proven OPEN and zero active source paths reach the fault. |

## 27.2 Evidence-Condition Branches

| Condition | Controlled evidence | Derived boundary result | Action treatment |
| --- | --- | --- | --- |
| A — trustworthy OPEN | GOOD, FRESH, valid timestamp, observed OPEN | PROVEN OPEN / SATISFIED | No OPEN command is required or offered. |
| B — trustworthy CLOSED | GOOD, FRESH, valid timestamp, observed CLOSED | PROVEN CLOSED | Offer an OPEN isolation action only when existing workflow and command gates authorise it. |
| C — untrustworthy or absent | STALE, UNCERTAIN, BAD, INVALID_TIMESTAMP, or missing required telemetry | UNPROVEN | Do not offer a redundant OPEN command. Present the evidence deficiency; isolation cannot be completed until trustworthy evidence is restored. |

Condition C never causes a redundant OPEN command merely because the reported state cannot be trusted. The workflow presents the exact telemetry deficiency and awaits a controlled valid update/refreshed observation. That update triggers the same full recalculation as a command. Source breakers opened by protection are processed through the same evidence conditions.

## 27.3 Formal and Exploration Application

In formal mode the generic workflow derives SW-A12 and SW-A23 for SEC-A2 and the approved deterministic procedure opens them in that order. After N2 proof, the existing next action remains BRK-A reclose to N3; alternate restoration assessment is not enabled until the N3 preconditions are met. In Exploration Mode, all eight represented sections use the same derivation and workflow, and feeder roles and outcomes remain run-specific and non-guaranteed.

## 27.4 Lifecycle Gate

DC-003 must be applied to every affected authoritative artefact and cross-document verified before final Step 9 acceptance and implementation authorisation. This lifecycle gate supersedes the former increment-specific draft wording. Implementation remains subject to a later explicit user authorisation.

V2 Automation Candidate — A future assurance workflow could automatically compare boundary/action records across revisions and select affected regression tests. V1 preserves the deterministic sequence and engineer-controlled evidence review.

# 28. Accepted Controlled Amendment — DC-005 Validation Suspension Workflow

This accepted workflow adds the missing controlled route for the five accepted suspension conditions. It does not change the formal N0–N5, negative telemetry, Exploration, defect/correction or operational-event workflows. A caller never selects BLOCKED-TEST; the validation-assurance authority derives it only from a finalised suspension record.

## 28.1 Actors and Authority

| Actor/function | Permitted responsibility | Prohibited action |
| --- | --- | --- |
| Graduate Engineer | Select controlled test/case; raise VSC-001/VSC-002 or pre-entry VSC-004 proposal with exact evidence; review backend-detected condition. | Self-finalise reviewer-controlled suspension; submit verdict/reason; use narrative instead of evidence. |
| Independent Engineering Reviewer | Finalise/reject judgement-based condition through a distinct controlled local actor_id/role after source/evidence review; engineering review asserts real identity/independence. | Use the proposer actor ID; claim that V1 authenticates a person or cryptographically proves organisational independence; override machine facts. |
| Backend Assurance | Resolve trusted target selection; separate target and verifier builds; classify deterministically; verify VSC-003/runtime VSC-004/VSC-005; generate reason; atomically finalise. | Infer engineering judgement; accept client test/case authority, arbitrary evidence or overlapping classification; create fictional run. |
| Operator/Reviewer UI | Present condition/evidence/authority state and submit permitted request/review action. | Calculate eligibility, choose BLOCKED-TEST or modify evidence membership after finalisation. |

## 28.2 Pre-Execution Entry Suspension

| Step | Actor/function | Controlled activity | Required result/record |
| --- | --- | --- | --- |
| SUS-PRE-01 | Campaign/test-selection authority / Validation | Create immutable target selection from the controlled campaign/test/case definition and requested input identities; record canonical selection hash. | Trusted intended target exists; client case_id text alone is insufficient; no run/execution created. |
| SUS-PRE-02 | Assurance authority | Verify target-selection authority, resolve available source identities, record failed required input role/presented evidence and keep assurance-verifier build separate from target application build. | If exact test/case cannot be proven, no case-level BLOCKED-TEST; attempt remains broader incomplete input-resolution work. |
| SUS-PRE-03 | Graduate Engineer / Reviewer or Backend | Evaluate the versioned semantic classification chain and exact evidence/authority contract. | Exactly one VSC ID or rejection; ordinary missing evidence remains incomplete; explicit PRE_EXECUTION_ENTRY. |
| SUS-PRE-04 | Assurance authority | Independently finalise judgement record or reproduce backend fact; generate reason/fingerprint including classifier and target anchor. | Immutable ValidationSuspensionRecord = BLOCKED-TEST; no fictional run/execution or ExecutedValidationResult. |

## 28.3 Suspension After Valid Entry

| Step | Controlled activity | Required result |
| --- | --- | --- |
| SUS-ACT-01 | Resolve the active ValidationAttempt, target selection, actual run/execution context, source catalogue/test/case/configuration and evidence class. | Target anchor and every available identity agree; target application and verifier builds remain distinct. |
| SUS-ACT-02 | Evaluate the deterministic single-condition classifier at EXECUTION_IN_PROGRESS or EVIDENCE_FINALISATION with mandatory evidence and authority. | Valid comparison creates PASS/FAIL; ordinary missing evidence remains non-finalisable/incomplete. |
| SUS-ACT-03 | Generate reason/fingerprint and atomically finalise suspension plus attempt/context relationship. | Attempt becomes terminal SUSPENDED/BLOCKED-TEST, retains evidence and creates no ExecutedValidationResult. |
| SUS-ACT-04 | If work is corrected/repeated, initialise a new controlled attempt. | Earlier suspension remains immutable; new run/execution/suspension identities are separate. |

## 28.4 Composite, Review and Export Workflow

For each DC-004 case the assembler accepts exactly one EXECUTION_RESULT or SUSPENSION_RESULT. A suspension occupies a required case only when its trusted target-selection authority/hash resolves against the accepted campaign and source catalogue/test/case definition; client case_id text cannot satisfy membership. The assembler verifies classifier, resolved sources, target/verifier build roles, class, evidence and any actual run/execution links. Missing, unanchored, unexecuted or invalid source remains INCOMPLETE; FAIL retains precedence.

Review displays the source kind and never collapses pre-entry suspension into a run. Export packages the finalised registry/record/evidence/authority/reason and any linked execution/run under original source identities plus separate generation build. FORMAL progress excludes every EXPLORATORY suspension/composite under QA-034. Operational events remain exactly 15.

## 28.5 Prohibited Shortcuts and Accepted Design Gate

Prohibited: caller-supplied target authority, verdict or controlled reason; unsupported/overlapping condition; HASH_MISMATCH as VSC-003; arbitrary notes/evidence; substituting verifier build for unresolved target build; fabricated run/result; reopening/reclassifying a final record; treating missing case/evidence as FAIL or BLOCKED-TEST; claiming cryptographic reviewer independence; turning operational BLOCKED into BLOCKED-TEST; adding an event; or resuming I9.

DC-005 and Section 28 are accepted as the authoritative validation-suspension workflow, and Workflow Design v0.3 supersedes v0.2 as the current workflow baseline. QA-041/QA-042 implementation and I9 remain stopped pending separate authorisation and independent review.

# 29. Proposed Controlled Amendment — DC-006 Validation Determination Workflow

This proposed Section 29 defines the controlled workflow that executes the accepted DC-006 methods without inventing engineering behaviour. Workflow Design v0.3 remains accepted until this proposed v0.4 application is independently reviewed and accepted.

## 29.1 Method Resolution and Entry

| Controlled field | Authoritative value / rule |
| --- | --- |
| DET-WF-01 Select target | Resolve the current controlled campaign/test and optional exact DC-004 case from the active future promoted Validation Catalogue. A composite parent cannot be selected for a direct DC-006 method. |
| DET-WF-02 Resolve definition | Resolve test/case/method/criteria by exact versions/hashes; verify evidence class, requirement mappings, context kind, roles and expected values before evidence capture. |
| DET-WF-03 Evaluate entry | Apply accepted Validation Plan entry criteria and DC-005 classifier. Ordinary missing context/evidence remains INCOMPLETE; only a genuine VSC condition may suspend as BLOCKED-TEST. |

## 29.2 Context Creation and Binding

| Controlled field | Authoritative value / rule |
| --- | --- |
| SCENARIO_EXECUTION | Initialise or bind exactly one real ScenarioRun and one ValidationExecution. Capture required checkpoints immediately from backend state. N0–N5 retains the exact T+0/10/11/20/30/40/50/55 chronology, one execution and six state checkpoints. |
| CONTROLLED_FIXTURE_EXECUTION | Resolve exact fixture version/hash and inputs; execute the authoritative service boundary; preserve fixture result/build; create no ScenarioRun and mutate no canonical package. |
| PRESERVED_RECORD_SET | Resolve every exact role-labelled immutable member and freeze membership before evaluation. Do not infer a missing member from current mutable state. |
| ENGINEERING_REVIEW | Bind exact build/surfaces/records/checklist and create one controlled review execution with proposer/final-reviewer authority state; create no ScenarioRun. |

## 29.3 Machine Criterion Evaluation

For each required machine criterion, Validation/Evidence resolves the definition-owned source adapter/selector, verifies identity/provenance/evidence class, applies the exact operator/normalisation and writes one immutable finding. A source resolution failure leaves the criterion NOT_EVALUATED and the attempt INCOMPLETE unless DC-005 validly classifies the condition. No test-ID, section-ID or case-ID outcome branch is permitted.

## 29.4 Reviewer Proposal and Finalisation

| Controlled field | Authoritative value / rule |
| --- | --- |
| Proposal | Eligible proposer binds the fixed proposition, exact evidence members and proposed SATISFIED/NOT_SATISFIED finding with reason; cannot edit proposition, criterion, target or aggregate. |
| Independent finalisation | Distinct eligible reviewer resolves the same identities/evidence, confirms or rejects the criterion finding and freezes actors/evidence/reason/hash atomically. |
| Boundary | Reviewer does not supply overall PASS/FAIL. Subjective NFR qualities remain reviewer propositions; machine criteria prove only presence/identity/linkage/structure/configuration facts. |

## 29.5 Incomplete, PASS and FAIL Finalisation

The backend verifies exact context membership, checkpoints, criterion set, source/evidence links and final findings once each. Any absent, duplicate, mismatched or unfinalised required item leaves the attempt INCOMPLETE with no ExecutedValidationResult. Complete any NOT_SATISFIED produces one immutable FAIL. Complete all SATISFIED produces one immutable PASS. A repeat starts a new attempt/context/finding/result chain.

## 29.6 DC-004 Composite Branch

For VT-EXP-ALL-001 and VT-EXP-ROLE-001, execute one case-scoped DC-006 method per exact required case, each with one EXPLORATION ScenarioRun/EXPLORATORY ValidationExecution. Do not create a parent method, context, execution or direct result. Assemble the existing DC-004 composite only from the exact required constituent result/suspension sources and retain existing completeness/precedence/immutability rules.

Static case mappings establish intended parent coverage; achieved PASS/FAIL evidence requires the complete executed finding chain. A suspended constituent may produce composite BLOCKED-TEST but its planned mappings are not reported as successfully verified. Unknown/non-required cases cannot supply parent coverage.

## 29.7 DC-005 Suspension Branch

At pre-entry, execution-in-progress or evidence-finalisation, the existing DC-005 target/classifier/evidence/authority workflow remains exclusive. Valid suspension creates no ExecutedValidationResult. Operational BLOCKED remains an engineering outcome and may satisfy a criterion. Missing ordinary evidence is INCOMPLETE. The DC-006 method/criterion identities and evidence become additional bound provenance; no sixth VSC condition is added.

## 29.8 Review, History and Export

Review shows context, expected/observed values, source selectors/records, finding status, requirement_ids, evidence links, completeness diagnostics and backend aggregate. Historical records resolve against their source Validation Catalogue identity; Network Configuration identity is separate. Export preserves full criterion/finding/evidence and DC-004/DC-005 membership chains plus separate source/generation build provenance.

## 29.9 Proposed Application Gate

DC-006 design decision is independently accepted. This Section 29 and proposed Workflow Design v0.4 are an authoritative-document application pending independent review. No machine Validation Catalogue promotion, application implementation or I9 resumption is authorised.