# System Requirements Specification

Operational Technology Graduate Demonstration Project
Document: System Requirements Specification
Version: 0.1
Status: Draft

# 1. Purpose

This System Requirements Specification defines the functional and supporting requirements for the fictional Operational Technology validation environment.

The requirements translate the approved project scope, engineering investigations and Engineering Design Brief into discrete statements of required system behaviour.

The specification will provide the principal technical baseline against which:

- the Network Model will be developed;

- the System Architecture will be defined;

- the demonstrator will be implemented;

- validation test cases will be written;

- validation results will be assessed;

- and requirement-to-test traceability will be maintained.

The requirements describe what the engineering solution must do, rather than prescribing unnecessary implementation details about how the software must achieve it.

# 2. Requirements Philosophy

Requirements will follow five principles.

## 2.1 Testable

Each functional requirement should describe behaviour that can later be objectively verified.

For example:

Weak

The system should realistically represent network topology.

This is difficult to test.

Better

The system shall determine the energisation state of each distribution section from the configured network connectivity and current switching-device states.

We can construct a known topology and verify the resulting section states.

## 2.2 Atomic Where Practical

A requirement should generally represent one principal behaviour.

For example, instead of:

The system shall calculate outages, customer impact, feeder loading and restoration eligibility.

we should create separate requirements for each behaviour.

This makes failures and traceability much clearer.

## 2.3 Implementation-Neutral

Requirements should avoid unnecessarily specifying software architecture.

For example:

Avoid:

The React frontend shall call a TypeScript topology function…

Use:

The system shall recalculate operational topology following a relevant switching-state change.

React and TypeScript would be implementation decisions, not engineering requirements.

## 2.4 Traceable

Every requirement will receive a stable identifier.

The proposed structure is:

REQ-NET-xxx  Network model

REQ-TOP-xxx  Topology / energisation

REQ-TEL-xxx  Telemetry

REQ-ALM-xxx  Alarm handling

REQ-OUT-xxx  Outage / customer impact

REQ-RST-xxx  Restoration

REQ-EVT-xxx  Events / audit

REQ-VAL-xxx  Validation support

REQ-CFG-xxx  Configuration / defect handling

REQ-NFR-xxx  Supporting non-functional requirements

This allows later relationships such as:

Engineering Decision

↓

REQ-TOP-003

↓

VT-TOP-003

↓

Test Evidence

↓

PASS / FAIL

## 2.5 Appropriate to the Project Boundary

The specification will not introduce requirements for capabilities intentionally excluded from the project, such as:

- protection coordination;

- fault-current calculations;

- detailed load flow;

- voltage analysis;

- real SCADA communications;

- crew dispatch;

- customer notifications;

- production cybersecurity;

- autonomous real-world switching.

This preserves the governing scope.

# 3. Requirement Priority

Because this is a deliberately bounded engineering package, we do not need a complicated prioritisation framework.

Requirements will use:

Mandatory — necessary to satisfy the defined project objectives and validation scenario.

Supporting — improves engineering traceability, usability or evidence quality but is not fundamental to the electrical/operational behaviour being demonstrated.

Unless otherwise stated, the functional requirements below are Mandatory.

# 4. Network Model Requirements

## REQ-NET-001 — Distribution Source

Requirement

The system shall represent one upstream zone-substation source capable of supplying both primary feeders.

Rationale

A defined source is required for topology-based energisation determination.

Verification method

Inspection and functional test.

## REQ-NET-002 — Primary Feeders

Requirement

The system shall represent two primary distribution feeders supplied from the zone-substation source.

Rationale

The project requires one affected feeder and one alternate feeder capable of supporting the restoration scenario.

Verification method

Inspection.

## REQ-NET-003 — Feeder Source Breakers

Requirement

Each primary feeder shall include a source breaker whose operational state can be represented as OPEN or CLOSED.

Rationale

The feeder-fault scenario depends on protection opening the affected feeder breaker and changing the network topology.

Verification method

Inspection and functional test.

## REQ-NET-004 — Distribution Sections

Requirement

Each feeder shall contain multiple identifiable distribution sections connected according to the configured network topology.

Rationale

Distribution sections provide the required abstraction for fault location, energisation, load, outage and restoration assessment.

Verification method

Inspection.

## REQ-NET-005 — Section Connectivity

Requirement

The network model shall explicitly represent connectivity relationships between distribution sections and switching devices.

Rationale

Operational topology must be derived from configuration rather than from hard-coded scenario outcomes.

Verification method

Configuration inspection and topology test.

## REQ-NET-006 — Section Load

Requirement

Each distribution section relevant to restoration shall have a defined simplified electrical load.

Rationale

Section loads are required to calculate transferable load during restoration assessment.

Verification method

Configuration inspection.

## REQ-NET-007 — Customer-Zone Association

Requirement

Each distribution section relevant to customer-impact calculation shall be associated with a defined customer zone containing a customer count.

Rationale

This supports derivation of affected customers from network energisation state.

Verification method

Configuration inspection.

## REQ-NET-008 — Normally-Open Tie

Requirement

The network shall include a switching device connecting the two feeder networks that is configured as normally open.

Rationale

The tie provides the alternate supply path required by the restoration scenario.

Verification method

Configuration inspection.

## REQ-NET-009 — Fault Isolation Capability

Requirement

The network shall include sufficient sectionalising capability to electrically isolate the predefined faulted section from a healthy section proposed for alternate restoration.

Rationale

Healthy load must not be restored through a path containing the faulted section.

Verification method

Network-model inspection and restoration test.

## REQ-NET-010 — Feeder Capacity

Requirement

Each feeder used in restoration assessment shall have a defined simplified operating capacity.

Rationale

The alternate-feeder capacity is required to determine whether proposed load transfer is acceptable.

Verification method

Configuration inspection.

## REQ-NET-011 — Consistent Sectionalising Structure

Requirement

Each primary feeder shall include a sectionalising switch between each pair of adjacent distribution sections represented in the simplified network model.

Rationale

Equivalent feeders should use a consistent sectional structure unless an engineering reason justifies a difference. This improves model coherence while retaining the same radial topology and restoration scope.

Verification method

Network-model inspection and configuration inspection.

# 5. Topology and Energisation Requirements

These are among the most important requirements in the project because they define how configuration and operational state become network behaviour.

## REQ-TOP-001 — Operational Topology Derivation

Requirement

The system shall derive the active operational topology from the configured network connectivity and current states of relevant switching devices.

Rationale

Operational topology must reflect both persistent network configuration and current field state.

Verification method

Functional test using known configurations and switching states.

## REQ-TOP-002 — Source-Path Energisation

Requirement

The system shall classify a distribution section as ENERGISED only where a continuous permitted electrical path exists between that section and an available source.

Rationale

Section energisation must follow network connectivity rather than a preassigned scenario state.

Verification method

Topology functional test.

## REQ-TOP-003 — Loss-of-Source Behaviour

Requirement

Where no valid path exists between a distribution section and an available source, the system shall classify the section as DE-ENERGISED.

Rationale

This defines the fundamental downstream consequence of feeder disconnection.

Verification method

Functional test.

## REQ-TOP-004 — Breaker-Trip Recalculation

Requirement

The system shall recalculate operational topology and section energisation following a feeder source-breaker state change.

Rationale

The initiating feeder trip must propagate through the operational network model.

Verification method

Scenario test.

## REQ-TOP-005 — Switching-State Recalculation

Requirement

The system shall recalculate operational topology and section energisation following a state change of any switching device that affects network connectivity.

Rationale

Isolation and restoration actions alter available supply paths.

Verification method

Functional switching test.

## REQ-TOP-006 — Fault and Energisation State Independence

Requirement

The system shall represent fault status independently from section energisation status.

Rationale

A healthy section may be de-energised following a feeder trip, while a faulted section must remain distinguishable from healthy de-energised sections.

Verification method

Configuration/state inspection and functional test.

## REQ-TOP-007 — Faulted Section Isolation

Requirement

The topology model shall support an operating state in which the predefined faulted section is electrically isolated from all available source paths.

Rationale

Isolation is required before healthy sections may be considered for alternate restoration.

Verification method

Topology functional test.

## REQ-TOP-008 — Alternate Supply

Requirement

Following valid fault isolation and restoration switching, the system shall be capable of deriving an energised state for a healthy section supplied from the alternate feeder through the tie connection.

Rationale

This is the principal restoration behaviour required by the project.

Verification method

Restoration scenario test.

## REQ-TOP-009 — Radial Topology Validation

Requirement

The system shall identify when a proposed restoration switching configuration creates an unintended energised loop contrary to the defined radial operating arrangement.

Rationale

The restoration assessment must prevent an invalid network configuration without requiring detailed parallel power-flow analysis.

Verification method

Negative restoration test.

# 6. Telemetry Requirements

## REQ-TEL-001 — Monitored Device State

Requirement

The system shall represent current operational states for monitored breakers and switching devices required by the validation scenario.

Rationale

Operational topology depends on current switching-device state.

Verification method

Inspection and functional test.

## REQ-TEL-002 — Telemetry Value

Requirement

Each monitored operational point shall contain a current or last-known value appropriate to the point type.

For switching devices, the relevant discrete values shall include OPEN and CLOSED.

Verification method

Inspection.

## REQ-TEL-003 — Telemetry Quality

Requirement

Each monitored operational point used in restoration assessment shall include a telemetry-quality state.

The demonstrator shall support, at minimum:

GOOD

UNCERTAIN

BAD

Rationale

A displayed value alone is insufficient to establish whether operational information is trustworthy.

Verification method

Inspection and functional test.

## REQ-TEL-004 — Telemetry Timestamp

Requirement

Each monitored operational point used in restoration assessment shall include the timestamp of its most recent update.

Rationale

The age of operational information is required to determine whether the point is sufficiently current for restoration assessment.

Verification method

Inspection.

## REQ-TEL-005 — Telemetry Age

Requirement

The system shall determine the age of required telemetry from the current scenario time and the point’s most recent update timestamp.

Conceptually:

Age = CurrentTime - LastUpdateTime

Verification method

Functional test using controlled timestamps.

## REQ-TEL-006 — Telemetry Freshness Threshold

Requirement

The system shall classify required telemetry as stale where its age exceeds the defined project-specific maximum allowable age.

Rationale

The Engineering Investigation established that staleness must be treated independently from reported telemetry quality.

Verification method

Boundary-value functional test.

Note

The numerical maximum age will be defined as a controlled project parameter later rather than embedded into this requirement.

## REQ-TEL-007 — Valid Operational Telemetry

Requirement

Telemetry required for restoration assessment shall be considered valid only where:

- its quality is GOOD; and

- its age does not exceed the defined maximum allowable age.

Verification method

Functional test.

## REQ-TEL-008 — Uncertain Telemetry

Requirement

The system shall not treat telemetry with quality UNCERTAIN as sufficient evidence of current switching-device state for restoration permission.

Rationale

Uncertain operational information must not be silently interpreted as reliable.

Verification method

Negative functional test.

## REQ-TEL-009 — Bad Telemetry

Requirement

The system shall not treat telemetry with quality BAD as sufficient evidence of current switching-device state for restoration permission.

Verification method

Negative functional test.

## REQ-TEL-010 — Stale Telemetry

Requirement

The system shall not treat stale telemetry as sufficient evidence of current switching-device state for restoration permission, even where the last reported quality is GOOD.

Rationale

This explicitly verifies the distinction between value quality and information freshness established during Engineering Investigation C.

Verification method

Negative functional test.

# 7. Why These Requirements Matter Together

The first three requirement groups now establish a very important dependency chain:

REQ-NET

defines what exists

↓

configured connectivity

+

REQ-TEL

defines what devices currently report

↓

REQ-TOP

derives operational network state

That gives us the foundation for everything that follows.

For example, after the feeder fault:

REQ-NET-005

Configured network connectivity

+

REQ-TEL-001

BRK-A = OPEN

↓

REQ-TOP-004

Topology recalculated

↓

REQ-TOP-003

Affected sections DE-ENERGISED

And this is also precisely why our intentional defect will work.

With the defective configuration:

Correct telemetry

+

Incorrect REQ-NET-005 configuration data

↓

Normal REQ-TOP logic

↓

Incorrect derived state

We are therefore building requirements that will let us later distinguish failure of a requirement implementation from correct processing of incorrect configuration data. That distinction will be important in the defect investigation.

Absolutely. We’ll continue the System Requirements Specification with the requirements for alarms, outage/customer impact, and restoration behaviour.

# 8. Alarm and Acknowledgement Requirements

## REQ-ALM-001 — Feeder Trip Alarm

Requirement

The system shall generate an operational alarm when the affected feeder breaker changes from CLOSED to OPEN as part of the defined feeder-fault scenario.

Rationale

The governing workflow requires an alarm to be generated following the feeder trip.

OT project definition.pdf

Verification method

Scenario test.

## REQ-ALM-002 — Alarm Identification

Requirement

Each generated alarm shall include sufficient information to identify:

- the alarm/event type;

- the affected asset;

- the alarm timestamp;

- the current alarm status.

Rationale

The operator must be able to associate the alarm with the relevant network event.

Verification method

Inspection.

## REQ-ALM-003 — Alarm Acknowledgement State

Requirement

The system shall represent whether an active alarm is acknowledged or unacknowledged.

Verification method

Functional test.

## REQ-ALM-004 — Operator Acknowledgement

Requirement

The system shall allow the operator to acknowledge the feeder-trip alarm.

Rationale

Operator acknowledgement is explicitly included in the governing operational workflow.

Verification method

Functional test.

## REQ-ALM-005 — Acknowledgement Record

Requirement

Acknowledgement of an alarm shall generate a traceable operational record including the alarm identifier, acknowledgement time and actor/origin.

Rationale

Operational actions must remain traceable through the project event history.

Verification method

Functional test and event-log inspection.

# 9. Outage and Customer-Impact Requirements

## REQ-OUT-001 — Outage Identification

Requirement

The system shall identify an outage where one or more customer-associated distribution sections are classified as DE-ENERGISED.

Rationale

The governing workflow requires outage identification following topology change.

Verification method

Scenario test.

## REQ-OUT-002 — Outage Extent

Requirement

The system shall maintain the set of currently de-energised customer-associated distribution sections as the current outage extent.

Verification method

Functional test.

## REQ-OUT-003 — Customer-Zone Mapping

Requirement

The system shall determine affected customer zones from their configured association with de-energised distribution sections.

Rationale

Customer impact must follow network state rather than a hard-coded fault-to-customer mapping.

Verification method

Functional test.

## REQ-OUT-004 — Affected-Customer Count

Requirement

The system shall calculate the current affected-customer count by summing the customer counts associated with customer zones supplied by currently de-energised sections.

Conceptually:

N_{affected}=\sum_{i=1}^{n}N_i

where N_i is the customer count associated with each affected customer zone.

Verification method

Calculated-result test.

## REQ-OUT-005 — Customer Impact Recalculation

Requirement

The system shall recalculate outage extent and affected-customer count following any topology change that alters section energisation.

Rationale

Customer impact must change as customers are de-energised or restored.

Verification method

Scenario test.

## REQ-OUT-006 — Restored Customers

Requirement

Where a previously de-energised customer-associated section becomes ENERGISED following valid restoration, its associated customers shall no longer be included in the current affected-customer count.

Verification method

Restoration scenario test.

## REQ-OUT-007 — Faulted Customers Remain Affected

Requirement

Customers associated with a section that remains faulted and isolated shall remain included in the current affected-customer count.

Rationale

Partial restoration must not incorrectly imply that all customers have been restored.

Verification method

Restoration scenario test.

# 10. Restoration Proposal Requirements

## REQ-RST-001 — Healthy Restorable Section Identification

Requirement

Following fault isolation, the system shall identify healthy DE-ENERGISED sections that may have a potential alternate-source path through the normally-open tie.

Rationale

The restoration process applies only to healthy portions of the affected feeder.

Verification method

Functional test.

## REQ-RST-002 — Candidate Restoration Proposal

Requirement

The system shall be capable of representing a candidate restoration proposal independently from the final restoration-permission decision.

Rationale

The governing workflow distinguishes restoration proposal from subsequent capacity and validity assessment.

Verification method

Functional test.

## REQ-RST-003 — Proposed Restoration Path

Requirement

A candidate restoration proposal shall identify the intended alternate source, tie connection and healthy section or sections proposed for restoration.

Verification method

Inspection.

# 11. Restoration Permissive Requirements

## REQ-RST-004 — Fault Isolation Permissive

Requirement

The system shall permit restoration only where the predefined faulted section is electrically isolated from the proposed alternate-supply path.

Verification method

Positive and negative restoration tests.

## REQ-RST-005 — Alternate Source Availability

Requirement

The system shall permit restoration only where a valid active path exists from an available alternate source to the proposed restored section or sections.

Verification method

Positive and negative restoration tests.

## REQ-RST-006 — Alternate Feeder Breaker State

Requirement

Where the alternate feeder source breaker is required for the proposed restoration path, its monitored state shall indicate CLOSED before restoration can be permitted.

Verification method

Negative restoration test.

## REQ-RST-007 — Radial Topology Permissive

Requirement

The system shall reject a restoration proposal where the resulting switching arrangement creates an unintended energised loop contrary to the defined radial operating arrangement.

Verification method

Negative restoration test.

## REQ-RST-008 — Telemetry Validity Permissive

Requirement

The system shall permit restoration only where every monitored switching-device state required to establish the proposed restoration topology satisfies REQ-TEL-007.

Verification method

Positive and negative restoration tests.

## REQ-RST-009 — Stale Telemetry Blocking

Requirement

The system shall classify the restoration assessment as BLOCKED where any required restoration telemetry is stale.

Rationale

The Project Vision explicitly requires stale telemetry to prevent unsafe action.

Verification method

Negative validation test.

## REQ-RST-010 — Uncertain Telemetry Blocking

Requirement

The system shall classify the restoration assessment as BLOCKED where any required restoration telemetry has quality UNCERTAIN.

Verification method

Negative validation test.

## REQ-RST-011 — Bad Telemetry Blocking

Requirement

The system shall classify the restoration assessment as BLOCKED where any required restoration telemetry has quality BAD.

Verification method

Negative validation test.

# 12. Transferable Load and Capacity Requirements

The governing Project Definition explicitly requires the project to support simplified engineering reasoning using feeder loading, transferable load, alternate-feeder capacity and resulting loading percentage.

## REQ-RST-012 — Transferable Load

Requirement

The system shall calculate proposed transferable load as the aggregate simplified load of healthy de-energised sections included in the candidate alternate-supply topology.

L_T=\sum_{i=1}^{n}L_i

where L_i is the simplified load of each section proposed for restoration.

Verification method

Calculated-result test.

## REQ-RST-013 — Existing Alternate-Feeder Load

Requirement

The restoration assessment shall use the defined current loading of the alternate feeder when performing the capacity check.

Verification method

Configuration inspection and calculated-result test.

## REQ-RST-014 — Resulting Feeder Load

Requirement

The system shall calculate resulting alternate-feeder loading as:

L_R=L_A+L_T

where:

- L_A = existing alternate-feeder load;

- L_T = transferable load.

Verification method

Calculated-result test.

## REQ-RST-015 — Loading Percentage

Requirement

The system shall calculate resulting feeder loading percentage as:

Loading\%=\frac{L_R}{C_A}\times100

where C_A is the defined alternate-feeder capacity.

Verification method

Calculated-result test.

## REQ-RST-016 — Capacity Permissive

Requirement

The restoration capacity permissive shall PASS where:

L_R\leq C_A

and shall FAIL where:

L_R>C_A

Verification method

Boundary-value calculated-result test.

## REQ-RST-017 — Capacity Rejection

Requirement

The system shall classify the restoration assessment as REJECTED where the resulting alternate-feeder load exceeds the defined alternate-feeder capacity.

Verification method

Negative restoration test.

# 13. Restoration Decision Requirements

## REQ-RST-018 — Permitted Outcome

Requirement

The system shall classify a restoration proposal as PERMITTED only where all applicable restoration permissive conditions pass.

At minimum, these shall include:

- fault isolation;

- alternate-source availability;

- topology validity;

- telemetry validity;

- feeder-capacity sufficiency.

Verification method

Positive restoration scenario test.

## REQ-RST-019 — Rejected Outcome

Requirement

The system shall classify a restoration proposal as REJECTED where sufficient information exists to complete the assessment but one or more defined engineering permissive conditions fail.

Verification method

Negative restoration test.

## REQ-RST-020 — Blocked Outcome

Requirement

The system shall classify a restoration proposal as BLOCKED where required operational information is insufficient or unreliable to support a safe assessment.

Verification method

Negative telemetry test.

## REQ-RST-021 — Assessment Reason

Requirement

A REJECTED or BLOCKED restoration result shall identify the permissive condition or conditions responsible for the outcome.

Rationale

The system must expose engineering reasoning rather than provide an unexplained final state.

Verification method

Inspection and functional test.

## REQ-RST-022 — Assessment Evidence

Requirement

The restoration assessment shall provide the relevant supporting values associated with each evaluated permissive where applicable.

For example:

- device state;

- telemetry quality;

- telemetry age;

- existing feeder load;

- transferable load;

- resulting load;

- feeder capacity;

- resulting loading percentage.

Verification method

Inspection.

# 14. Simulated Restoration Requirements

## REQ-RST-023 — Restoration Execution Control

Requirement

The system shall allow the simulated restoration switching action to be initiated only where the restoration assessment status is PERMITTED.

Rationale

The demonstrator must not bypass its own restoration validation logic.

Verification method

Positive and negative functional tests.

## REQ-RST-024 — No Real Equipment Control

Requirement

All switching actions represented within the demonstrator shall be simulated and shall not interface with real operational equipment.

Verification method

Design inspection.

## REQ-RST-025 — Tie State Change

Requirement

Where permitted restoration requires use of the normally-open tie, simulated restoration shall change the tie’s operational state from OPEN to CLOSED.

Verification method

Restoration scenario test.

## REQ-RST-026 — Post-Restoration Topology Recalculation

Requirement

Following simulated restoration switching, the system shall recalculate operational topology and section energisation.

Verification method

Scenario test.

## REQ-RST-027 — Healthy Section Re-Energisation

Requirement

Healthy de-energised sections included in the valid restoration path shall be classified as ENERGISED following successful simulated restoration.

Verification method

Scenario test.

## REQ-RST-028 — Faulted Section Remains De-Energised

Requirement

The predefined faulted section shall remain DE-ENERGISED following restoration of healthy sections through the alternate feeder.

Verification method

Scenario test.

## REQ-RST-029 — Post-Restoration Customer Recalculation

Requirement

The system shall recalculate affected-customer count following successful simulated restoration.

Verification method

Scenario test.

# 15. Requirement Dependency Example

The restoration logic now has a clear requirement hierarchy.

For example:

REQ-TEL-003

Telemetry quality exists

↓

REQ-TEL-007

Telemetry validity determined

↓

REQ-RST-008

Telemetry permissive evaluated

↓

REQ-RST-018

Restoration PERMITTED only if it passes

Likewise:

REQ-NET-006

Section loads defined

↓

REQ-RST-012

Transferable load calculated

↓

REQ-RST-014

Resulting feeder load calculated

↓

REQ-RST-015

Loading percentage calculated

↓

REQ-RST-016

Capacity pass/fail

↓

REQ-RST-018 / 019

Final decision

This is exactly the traceability we want later.

A failed restoration outcome will not simply say “no.” We will be able to trace the decision back through the individual engineering requirements that produced it.

# 16. Operational Event and Audit Requirements

## REQ-EVT-001 — Operational Event Creation

Requirement

The system shall create an operational event record for significant simulated operational actions and state changes within the defined feeder-fault workflow.

Rationale

The governing Project Definition requires operational events to be recorded correctly, and the project Vision requires engineering actions to remain traceable through system logs.

Verification method

Scenario test and event-log inspection.

## REQ-EVT-002 — Event Identifier

Requirement

Each operational event shall have a unique event identifier.

Verification method

Inspection.

## REQ-EVT-003 — Event Timestamp

Requirement

Each operational event shall include the time at which the represented action or state change occurred.

Verification method

Inspection.

## REQ-EVT-004 — Event Source

Requirement

Each operational event shall identify the conceptual system or function responsible for the event.

Supported sources shall include, where applicable:

- SCADA;

- ADMS;

- OMS;

- Operator;

- validation-support function.

Rationale

The event record should make the cross-system operational sequence visible.

Verification method

Inspection.

## REQ-EVT-005 — Event Type

Requirement

Each operational event shall include an event type sufficient to classify the represented activity.

Examples may include:

DEVICE_STATE_CHANGE

ALARM_GENERATED

ALARM_ACKNOWLEDGED

TOPOLOGY_RECALCULATED

OUTAGE_UPDATED

RESTORATION_ASSESSED

SWITCHING_ACTION

The final event-type set may be refined during detailed implementation.

Verification method

Inspection.

## REQ-EVT-006 — Affected Entity

Requirement

Where an operational event relates to a specific network or operational entity, the event shall identify that entity using its stable identifier.

Verification method

Inspection.

## REQ-EVT-007 — State Transition

Requirement

Where an event represents a discrete state transition, the event shall record the previous and new values where applicable.

For example:

BRK-A

Previous: CLOSED

New: OPEN

Verification method

Scenario test.

## REQ-EVT-008 — Chronological Event History

Requirement

The system shall make operational events available in chronological sequence.

Rationale

The graduate engineer must be able to reconstruct the operational progression of a validation scenario.

Verification method

Scenario inspection.

## REQ-EVT-009 — Alarm Acknowledgement Traceability

Requirement

Alarm acknowledgement shall be identifiable within the operational event history.

Verification method

Scenario test.

## REQ-EVT-010 — Restoration Assessment Traceability

Requirement

Execution of a restoration assessment shall create or preserve a traceable record of:

- assessment result;

- assessment time;

- candidate restoration path;

- relevant permissive outcomes.

Verification method

Functional test and record inspection.

## REQ-EVT-011 — Switching Traceability

Requirement

Each simulated switching operation performed during isolation or restoration shall be represented in the operational event history.

Verification method

Scenario test.

# 17. Engineering Validation Requirements

The following requirements relate specifically to the graduate engineering validation package rather than normal simulated utility operation.

The governing Project Definition assigns the graduate responsibility for executing test cases, comparing expected and observed behaviour, recording results, identifying failures, investigating issues, correcting them and repeating validation.

## REQ-VAL-001 — Validation Test Identification

Requirement

Each formal validation test shall have a unique test identifier.

Verification method

Documentation inspection.

## REQ-VAL-002 — Requirement Traceability

Requirement

Each formal validation test shall identify the engineering requirement or requirements that it verifies.

Rationale

This establishes traceability between the requirements baseline and validation evidence.

Verification method

Traceability inspection.

## REQ-VAL-003 — Test Objective

Requirement

Each validation test shall define the behaviour or engineering condition being verified.

Verification method

Documentation inspection.

## REQ-VAL-004 — Defined Initial Conditions

Requirement

Each validation test shall specify the required initial network, configuration and operational conditions necessary for repeatable execution.

Verification method

Documentation inspection and repeatability test.

## REQ-VAL-005 — Configuration Version

Requirement

Each validation execution shall identify the network/configuration version against which the test was performed.

Rationale

The project must distinguish results obtained using the defective baseline from results obtained after correction.

Verification method

Validation-record inspection.

## REQ-VAL-006 — Expected Result

Requirement

Each validation test shall define the expected engineering result before execution.

Verification method

Documentation inspection.

## REQ-VAL-007 — Observed Result

Requirement

Each executed validation test shall record the observed result produced by the demonstrator.

Verification method

Validation-record inspection.

## REQ-VAL-008 — Pass/Fail Determination

Requirement

Each executed validation test shall be assigned a PASS or FAIL result based on comparison of expected and observed behaviour.

Verification method

Functional/documentation inspection.

## REQ-VAL-009 — Evidence Reference

Requirement

Each executed validation test shall reference sufficient supporting evidence to justify its recorded outcome.

Supporting evidence may include:

- telemetry state;

- topology state;

- section energisation;

- customer-impact calculation;

- restoration assessment;

- event records;

- configuration information.

Verification method

Validation-package inspection.

## REQ-VAL-010 — Failed Test Preservation

Requirement

A validation test that fails because of the intentional engineering defect shall remain preserved in the engineering record after the defect is corrected.

Rationale

The failed result forms part of the evidence demonstrating investigation and corrective action.

Verification method

Documentation inspection.

## REQ-VAL-011 — Repeat Validation

Requirement

Following correction of the intentional engineering defect, the affected validation test shall be executable again using the corrected configuration.

Verification method

Repeat validation.

## REQ-VAL-012 — Corrected Result Preservation

Requirement

The result of repeat validation using the corrected configuration shall be recorded separately from the original failed execution.

Verification method

Validation-record inspection.

## REQ-VAL-013 — Negative Test Interpretation

Requirement

The validation framework shall support tests where correct system behaviour results in an operational action being BLOCKED or REJECTED.

Rationale

For example, stale telemetry causing restoration to be BLOCKED is an expected safety-oriented behaviour and should result in an engineering test PASS.

Verification method

Negative validation test.

## REQ-VAL-014 — Scenario Reset

Requirement

The demonstrator shall support resetting a validation scenario to a defined initial state sufficient to allow controlled repeat execution.

Verification method

Repeatability test.

# 18. Defect Investigation and Configuration Requirements

## REQ-CFG-001 — Seeded Defect Type

Requirement

The validation baseline shall contain one intentional incorrect network-topology connection within the configured distribution network model.

Rationale

This implements the defect selected during Engineering Investigation D.

Verification method

Controlled configuration inspection.

## REQ-CFG-002 — Configuration-Based Failure

Requirement

The intentional defect shall exist in network configuration data rather than in special-case application logic designed to force an incorrect validation result.

Verification method

Design/code/configuration inspection.

## REQ-CFG-003 — Normal Processing of Defective Configuration

Requirement

The same topology-processing logic shall be used for both defective and corrected network configurations.

Rationale

The defect investigation must demonstrate incorrect source configuration being processed normally rather than an artificial software failure mode.

Verification method

Code/design inspection and comparative test.

## REQ-CFG-004 — Observable Downstream Impact

Requirement

The seeded topology defect shall cause at least one incorrect derived section-energisation result during the affected validation scenario.

Verification method

Validation test.

## REQ-CFG-005 — Customer-Impact Propagation

Requirement

The incorrect derived energisation caused by the seeded defect shall propagate to an incorrect outage or affected-customer result.

Rationale

This produces a cross-system validation failure suitable for engineering investigation.

Verification method

Scenario test.

## REQ-CFG-006 — Correct Telemetry During Defect Scenario

Requirement

The relevant initiating SCADA telemetry used during the seeded-defect validation scenario shall remain correct and valid.

Rationale

The investigation should be capable of ruling out telemetry error and tracing the failure to network configuration.

Verification method

Telemetry inspection.

## REQ-CFG-007 — Defect Identification

Requirement

The engineering validation package shall support identification of the incorrect configured connectivity relationship as the root cause of the failed test.

Verification method

Defect-investigation review.

## REQ-CFG-008 — Corrective Configuration

Requirement

A corrected network configuration shall be produced in which the erroneous topology relationship is replaced by the intended relationship.

Verification method

Configuration inspection.

## REQ-CFG-009 — Defective Configuration Preservation

Requirement

The original defective network configuration shall remain identifiable after correction.

Verification method

Configuration-control inspection.

## REQ-CFG-010 — Corrected Configuration Preservation

Requirement

The corrected network configuration shall be maintained as a separately identifiable configuration version.

Verification method

Configuration-control inspection.

## REQ-CFG-011 — Correction Record

Requirement

The defect investigation shall record:

- the identified configuration issue;

- the engineering effect of the issue;

- the corrective change applied;

- the affected configuration version;

- the resulting corrected version.

Verification method

Defect-report inspection.

## REQ-CFG-012 — Correction Verification

Requirement

The intentional defect shall not be considered resolved until the originally failed validation test passes using the corrected configuration.

Rationale

Applying a correction and verifying that the correction resolves the issue are separate engineering activities.

Verification method

Repeat validation.

# 19. Supporting Non-Functional Requirements

These requirements are intentionally limited. The project does not need enterprise-level software non-functional requirements because the demonstrator exists to support the engineering package, not to function as a production platform.

## REQ-NFR-001 — Engineering Clarity

Priority: Supporting

Requirement

The demonstrator shall present network, operational and validation information clearly enough for a reviewer to understand the engineering basis of the displayed outcome.

Verification method

Engineering review.

## REQ-NFR-002 — Stable Identifiers

Requirement

Significant engineering entities shall use stable identifiers that remain consistent across relevant documentation, implementation and validation evidence.

This includes, where applicable:

- feeders;

- breakers;

- switches;

- sections;

- customer zones;

- requirements;

- validation tests;

- events;

- defect records.

Verification method

Cross-document inspection.

## REQ-NFR-003 — Deterministic Validation Behaviour

Requirement

Given the same configuration version, initial state and validation inputs, the demonstrator shall produce the same engineering outcome.

Rationale

Repeatable validation requires predictable scenario behaviour.

Verification method

Repeat-execution test.

## REQ-NFR-004 — Fictional Data Only

Requirement

The demonstrator and supporting engineering package shall use fictional network, asset, operational and customer information.

Verification method

Documentation/configuration review.

## REQ-NFR-005 — Conceptual OT Representation

Requirement

The demonstrator shall not present its SCADA, ADMS, OMS or GIS representations as replicas of specific commercial or proprietary utility platforms.

Rationale

The governing documents explicitly define these as conceptual representations.

Verification method

Engineering/documentation review.

## REQ-NFR-006 — Simulated Operation Only

Requirement

The demonstrator shall not require or provide interfaces to real utility operational equipment.

Verification method

Design inspection.

## REQ-NFR-007 — Engineering-First Interface

Priority: Supporting

Requirement

Interface functionality shall be included where it supports network understanding, operational reasoning, validation, investigation, traceability or engineering evidence.

Features whose primary purpose is unrelated visual or software sophistication shall not be required.

Rationale

The governing Project Decisions explicitly establish “Engineering first, Software second” and require the software to support the engineering workflow rather than showcase frontend development.

Verification method

Design review.

## REQ-NFR-008 — Reviewability

Priority: Supporting

Requirement

The completed engineering package shall allow a reviewer to trace a validation result from the relevant requirement through the observed operational evidence and, where applicable, the associated defect/correction record.

Verification method

Traceability review.

## REQ-NFR-009 — Consistent Entity Modelling

Priority: Supporting

Requirement

Engineering entities representing the same class of network or operational object shall use a consistent modelling structure and information set unless a documented engineering reason requires otherwise.

Rationale

Consistent entity modelling improves professional coherence, reduces arbitrary implementation differences and supports generic processing across equivalent assets while still allowing legitimate configuration differences.

Verification method

Cross-model and implementation review.

# 20. Requirements Summary

The System Requirements Specification now contains the following requirement groups:

| Group | Scope |
| --- | --- |
| REQ-NET | Simplified distribution network and network data |
| REQ-TOP | Topology and section energisation |
| REQ-TEL | Operational telemetry quality, timestamp and freshness |
| REQ-ALM | Feeder alarm and acknowledgement |
| REQ-OUT | Outage extent and affected customers |
| REQ-RST | Restoration proposal, permissives, capacity and switching |
| REQ-EVT | Operational event history and auditability |
| REQ-VAL | Engineering validation and evidence |
| REQ-CFG | Intentional defect, correction and configuration control |
| REQ-NFR | Supporting engineering-quality constraints |

We now have 116 formal requirements across those groups.

That sounds like a relatively large number for a small project, but an important point is that these are deliberately atomic requirements. We have not created 114 software features. Many describe individual conditions within one small end-to-end workflow.

For example, the entire project still essentially does this:

NETWORK + TELEMETRY

↓

TOPOLOGY

↓

OUTAGE

↓

CUSTOMER IMPACT

↓

RESTORATION ASSESSMENT

↓

SIMULATED RESTORATION

↓

VALIDATION

↓

DEFECT INVESTIGATION

↓

CORRECTION

↓

REVALIDATION

The number of requirements exists so that each part of that chain can be tested and traced independently.

# 21. Verification Method Summary

The requirements use a small set of verification methods.

### Inspection

Used where compliance can be demonstrated by reviewing configuration, documentation or recorded information.

Examples:

- network contains two feeders;

- telemetry includes a timestamp;

- events contain stable identifiers.

### Functional Test

Used where the demonstrator must produce a defined behaviour in response to controlled inputs.

Examples:

- breaker state changes trigger topology recalculation;

- alarm acknowledgement changes state.

### Scenario Test

Used where several functions interact through the end-to-end operational workflow.

Examples:

- feeder trip causes downstream outage;

- restoration re-energises healthy sections.

### Calculated-Result Test

Used where a numerical engineering result can be independently calculated and compared.

Examples:

- affected-customer total;

- transferable load;

- resulting feeder loading percentage.

### Boundary-Value Test

Used where behaviour changes at an explicit engineering threshold.

Example:

L_R = C_A

must pass the capacity criterion, whereas:

L_R > C_A

must fail it.

Telemetry freshness can later be tested similarly around the defined maximum age.

### Engineering Review

Used for requirements whose quality depends on whether the engineering information is understandable and traceable rather than on a single Boolean software condition.

# 22. Requirements Baseline

This specification should now become the requirements baseline for the next stages of design.

However, I would label it:

Version 0.1 — Draft Engineering Baseline

rather than pretending it is permanently frozen.

The next stage—the detailed Network Model—may reveal that a requirement needs minor clarification. For example, once we choose the exact sectionalising arrangement, we may discover that terminology such as “faulted section isolated from all available source paths” needs to be expressed slightly more precisely.

If that occurs, we should use controlled revision:

Requirement identified

↓

Design conflict or ambiguity discovered

↓

Reason documented

↓

Requirement amended

↓

Version updated

↓

Affected downstream artefacts reviewed

We should not casually rewrite requirements during implementation simply because the code is easier another way.

That difference is part of the engineering discipline this project is trying to demonstrate.

# 23. Requirements Traceability Direction

We do not need to build the complete Requirements Traceability Matrix yet.

But from this point onward, every major engineering artefact should start referencing these requirement IDs.

For example, our later Network Model might contain:

Sectionalising Switch SW-A23

Supports:

REQ-NET-009

REQ-TOP-007

REQ-RST-004

Our later validation test might contain:

VT-RST-004

Fault Isolation Restoration Test

Verifies:

REQ-RST-004

REQ-RST-018

REQ-RST-023

And the intentional defect test could eventually show:

VT-TOP-DEF-001

Expected:

REQ-TOP-003 satisfied

Observed:

Section remains incorrectly energised

Result:

FAIL

Defect:

DEF-001

Corrected configuration:

v1.1

Repeat result:

PASS

That’s where the documentation will start feeling like one engineering package rather than several independently generated documents.

## End of System Requirements Specification