# Engineering Design Brief

Operational Technology Graduate Demonstration Project
Document: Engineering Design Brief
Version: 0.1
Status: Draft

# 1. Purpose

This Engineering Design Brief defines the proposed engineering solution for the fictional Operational Technology validation work package.

The purpose of the design is to establish a simplified but technically coherent environment in which a graduate engineer can validate the behaviour of an upgraded electricity-distribution operational workflow.

The design will support a single feeder-fault scenario progressing through:

fault occurrence → feeder protection operation → operational-state update → topology recalculation → outage identification → affected-customer assessment → restoration assessment → simulated restoration → event recording and validation.

The resulting solution is not intended to reproduce a commercial Distribution Control System, SCADA platform, ADMS, OMS or GIS implementation.

Instead, it will provide the minimum network model, operational-system representations, engineering logic and software functionality necessary to support the validation activities defined by the project. This is consistent with the governing requirement that the operational systems remain conceptual representations and that the interface support engineering validation rather than frontend development.

The design is therefore driven primarily by:

- engineering traceability;

- understandable network behaviour;

- explicit operational reasoning;

- repeatable validation;

- defect investigation;

- and clear technical communication.

Software implementation will remain subordinate to those objectives.

# 2. Design Basis

The engineering design is based on three sources of project authority:

### 2.1 Governing Project Documents

The Project Vision, Project Definition and Project Decisions establish the purpose, scope and fixed boundaries of the work package.

The project represents a small fictional graduate contribution within a broader electricity-distribution Operational Technology upgrade. The graduate engineer is responsible for understanding the network and information flows, executing validation, investigating unexpected behaviour, correcting an identified issue and verifying the corrected system.

The design must therefore support those activities directly.

### 2.2 Engineering Investigation Findings

Engineering Investigation Packages A–D established the technical principles required to make the fictional environment coherent.

Those investigations concluded that the design should use:

- a normally radial distribution network;

- two primary feeders connected through a normally-open tie;

- topology-derived section energisation;

- aggregated customer zones;

- conceptual separation of GIS/network configuration, SCADA telemetry, ADMS topology processing and OMS outage processing;

- fault isolation prior to alternate restoration;

- explicit restoration permissive checks;

- feeder-capacity assessment;

- telemetry quality and freshness;

- and an intentionally incorrect topology connection as the seeded engineering defect.

These findings form the technical basis of this Design Brief.

### 2.3 Project Scope Constraints

The design must remain proportionate to a graduate-level validation package.

It will therefore not require:

- detailed protection studies;

- load-flow modelling;

- voltage analysis;

- fault-current calculation;

- production-grade FLISR optimisation;

- vendor-specific OT implementation;

- real utility data;

- or direct control of physical equipment.

This limitation is deliberate. The governing documents explicitly state that the project is not intended to demonstrate mastery of proprietary utility software or advanced power-system analysis.

# 3. Design Objectives

The engineering solution shall be designed to satisfy the following objectives.

## 3.1 Represent an Understandable Distribution Network

The network must be sufficiently realistic to demonstrate:

- feeder supply;

- switching;

- radial operation;

- feeder loss;

- section de-energisation;

- fault isolation;

- tie restoration;

- transferred load;

- and customer impact.

At the same time, it must remain small enough that a reviewer can understand the entire network and manually reason about the expected state.

The governing Project Definition explicitly requires a simplified network that can be completely understood while still representing real distribution-system concepts.

## 3.2 Derive Operational Behaviour From Engineering State

The demonstrator should avoid pre-programmed outcomes wherever the project can reasonably derive them from the model.

For example, the system should not contain logic equivalent to:

“Feeder A fault means 700 customers lose supply.”

Instead:

breaker state

+

network connectivity

+

switching states

↓

active topology

↓

section energisation

↓

affected customer zones

↓

affected customer count

This design principle ensures that observed results arise from the engineering model rather than being merely scripted visual behaviour.

## 3.3 Demonstrate OT System Interaction

The solution must demonstrate how several operational functions contribute to a common network event.

The Project Vision specifically requires simplified representation of SCADA telemetry, topology, feeder status, alarms, outage information, operational workflows, event logging, engineering validation and defect investigation.

The design should therefore make system responsibility visible rather than hiding the entire workflow behind a single application function.

## 3.4 Support Engineering Validation

The solution must provide sufficient observable information to compare:

expected behaviour against observed behaviour.

A reviewer should be able to determine why a validation test passed or failed by examining relevant operational states, calculations and event records.

The system should therefore expose engineering evidence rather than only final outcomes.

## 3.5 Support Root-Cause Investigation

The seeded configuration defect must result in a genuine incorrect derived outcome.

The engineer should be able to trace the failure through:

observed incorrect result

↓

affected-customer information

↓

section energisation

↓

operational topology

↓

configured connectivity

↓

incorrect network-model relationship

Correction of the underlying configuration should resolve the observed behaviour without modification of the topology-processing algorithm.

This directly supports the project’s required validation → investigation → correction → revalidation lifecycle.

## 3.6 Maintain Traceability

The engineering solution must support traceability between:

project objective

↓

engineering requirement

↓

network/system design

↓

implemented behaviour

↓

validation test

↓

validation result

Significant operational events, engineering assumptions, test results and defect corrections should remain identifiable throughout the package.

This reflects the graduate responsibilities to document validation evidence, maintain traceability and communicate findings.

## 3.7 Remain Appropriate to Graduate-Level Contribution

The design should resemble something a graduate engineer could contribute to under supervision rather than something they would independently own as a production OT architect.

The graduate’s role is primarily to:

- understand the defined system;

- document its expected behaviour;

- validate it;

- investigate anomalies;

- identify configuration issues;

- recommend/apply a controlled correction within the fictional package;

- and demonstrate successful revalidation.

This distinction should remain visible throughout the project.

# 4. Overall Solution Concept

The proposed solution consists of five interacting conceptual layers.

┌──────────────────────────────────────────────┐

│        ENGINEERING VALIDATION LAYER          │

│ Test cases / evidence / defect investigation │

└──────────────────────┬───────────────────────┘

│

┌──────────────────────▼───────────────────────┐

│        OPERATIONAL WORKFLOW LAYER            │

│ Alarm / outage / restoration / event history │

└──────────────────────┬───────────────────────┘

│

┌──────────────────────▼───────────────────────┐

│     OPERATIONAL APPLICATION FUNCTIONS        │

│ SCADA │ ADMS │ OMS │ GIS/network information │

└──────────────────────┬───────────────────────┘

│

┌──────────────────────▼───────────────────────┐

│          NETWORK STATE / LOGIC               │

│ Connectivity / topology / energisation       │

│ isolation / feeder capacity / telemetry      │

└──────────────────────┬───────────────────────┘

│

┌──────────────────────▼───────────────────────┐

│      SIMPLIFIED DISTRIBUTION NETWORK         │

│ Source / feeders / sections / switches       │

│ loads / customer zones                       │

└──────────────────────────────────────────────┘

These are conceptual design layers, not necessarily separate software services or applications.

That distinction is important.

The project should represent functional separation without adding unnecessary deployment complexity.

# 5. Simplified Distribution Network Concept

The physical-network abstraction will consist of:

ZONE SUBSTATION

/          \

/            \

FEEDER A              FEEDER B

BREAKER               BREAKER

│                     │

│                     │

Sections A             Sections B

│                     │

│                     │

└────── TIE ──────────┘

normally open

Each feeder will supply a small number of distribution sections under normal operation.

The two feeders will be interconnected at a suitable point by one normally-open tie switch.

The network will normally operate radially, meaning that each energised section has one intended active supply path from the zone substation.

The exact number, sequence and identifiers of sections will be defined during Step 5 — Network Model rather than in this Design Brief.

This is intentional: the Design Brief establishes how the network must behave, while the Network Model will establish exactly what assets and connections exist.

# 6. Network Element Design

The following element types are required at design level.

## 6.1 Zone Substation / Source

The zone substation will represent the upstream electricity supply available to both primary feeders.

Only the supply relationship relevant to the scenario will be represented.

Internal busbar configuration, transformers and transmission-side connections will not be modelled unless later found necessary to support a specific requirement.

For topology purposes, the zone substation behaves as an available energised source.

## 6.2 Primary Feeders

Two primary feeders will originate from the common source.

Each feeder will include, at minimum:

- feeder identifier;

- feeder name;

- feeder breaker;

- connected distribution sections;

- defined operating capacity;

- calculated or configured present loading.

The second feeder will serve as the alternate source for restoration of an eligible healthy portion of the first feeder.

## 6.3 Feeder Breakers

Each feeder will have a source breaker represented by a discrete operational state:

OPEN

CLOSED

Breaker state will be treated as monitored operational information supplied through the conceptual SCADA function.

Opening the affected feeder breaker following the simulated protection operation will remove the normal source path to its downstream sections.

Detailed breaker and protection characteristics are outside scope.

## 6.4 Distribution Sections

The feeder will be divided into discrete distribution sections.

A distribution section is the principal unit against which the project will reason about:

- network connectivity;

- fault location;

- energisation;

- isolation;

- load;

- restoration;

- and customer impact.

This abstraction deliberately avoids modelling individual conductors, poles or distribution transformers.

Each section will later require, at minimum:

Section identifier

Configured connectivity

Associated feeder

Simplified load

Fault status

Derived energisation state

Customer-zone association

Where switching boundaries are required to isolate a section, those boundaries will be explicitly represented.

## 6.5 Sectionalising Devices

Each primary feeder will include sectionalising switches between adjacent distribution sections. This provides a consistent switching structure across the two feeder models and allows network portions to be independently separated where required.

For the selected validation scenario, the switches immediately upstream and downstream of the predefined faulted section will be used to electrically isolate that section before restoration. Sectionalising devices elsewhere in the network will normally remain closed but will remain part of the configured topology and monitored operational state.

The detailed number, identifiers and locations of these devices will be defined in the Network Model.

This requirement emerged from Engineering Investigation A and C.

It would be technically inconsistent to restore a healthy downstream section through the alternate feeder while leaving an electrical path through the fault.

The final device arrangement will therefore provide a means to isolate the faulted section before alternate supply is established.

The Design Brief intentionally does not yet specify the exact number or location of sectionalising switches; those will be selected when the detailed Network Model is created.

## 6.6 Normally-Open Tie Switch

One normally-open tie switch will connect a suitable section of Feeder A with a suitable section of Feeder B.

Under the normal operating state:

Tie switch = OPEN

Under an eligible restoration state:

Tie switch = CLOSED

Closing the tie will only be permitted after the defined restoration conditions have been assessed.

The tie therefore provides an alternate electrical path; it does not itself determine whether restoration is safe or valid.

## 6.7 Customer Zones

Customers will be represented as aggregated customer zones rather than individual customer records.

Each customer zone will be associated with a distribution section and will contain at least:

Zone identifier

Associated network section

Customer count

A simplified load may either remain a property of the distribution section or be linked to the customer zone depending on the detailed Network Model.

The affected-customer result will be derived by summing customer counts associated with currently de-energised sections.

This achieves the required outage-impact behaviour without introducing unnecessary customer-management functionality.

# 7. Network-State Design

The solution will distinguish three kinds of network information.

### Configured state

What the network model says is connected to what.

Example:

Section A2 → Section A3

Tie TS-01 → A3 / B3

### Observed operational state

What monitored devices currently report.

Example:

BRK-A = OPEN

TS-01 = OPEN

### Derived operational state

What follows when configured connectivity and observed state are evaluated together.

Example:

A1 = DE-ENERGISED

A2 = DE-ENERGISED

A3 = DE-ENERGISED

This distinction is one of the core architectural principles of the design.

It enables the project to demonstrate how correct telemetry can still produce an incorrect operational result when the underlying network configuration is wrong—the exact behaviour required for the seeded defect investigation.

# 8. Energisation Design

Section energisation shall be determined dynamically.

The project will use the following simplified rule:

A section is energised when a continuous permitted path exists from an available source to that section through the configured network and the current states of all relevant switching devices allow supply.

Conceptually:

AVAILABLE SOURCE

↓

closed/permitted device?

↓

connected section

↓

closed/permitted device?

↓

next section

If no valid source path exists:

section = DE-ENERGISED

If a valid source path exists:

section = ENERGISED

The application should therefore recalculate energisation following relevant topology-changing events rather than permanently assigning energisation to a section.

This design supports the governing validation requirement that topology update correctly and downstream sections become de-energised following the feeder event.

# 9. Conceptual OT System Architecture

The demonstrator will represent four principal Operational Technology functions together with a separate engineering-validation function:

- SCADA

- GIS / network configuration

- ADMS

- OMS

- Engineering validation and evidence

These functions are conceptual responsibilities rather than separate commercial products or deployed services.

That distinction is important because the governing Project Definition explicitly states that the operational systems are conceptual representations whose purpose is to demonstrate system interaction rather than reproduce commercial software.

The proposed functional architecture is:

This architecture is deliberately simple. It preserves functional ownership while avoiding unnecessary software-service complexity.

# 9.1 SCADA Function

The SCADA representation will provide the operational environment with monitored field-state information.

For the selected scenario, SCADA will be responsible for representing:

- feeder breaker state;

- relevant sectionalising-switch states;

- tie-switch state;

- telemetry quality;

- telemetry timestamps;

- relevant alarms;

- operator alarm acknowledgement;

- state-change events.

SCADA will represent the observed operational state.

It will not calculate downstream section energisation or customer impact.

For example:

SCADA knows:

BRK-A = OPEN

TS-01 = OPEN

SW-A2 = CLOSED

but it does not directly state:

A3 = DE-ENERGISED

495 customers affected

Those are derived consequences that require network context.

This separation supports the design objective of making system interaction visible rather than treating all operational information as one undifferentiated application state.

# 9.2 GIS / Network Configuration Function

The GIS/network-configuration function will represent persistent network information.

It will provide:

- asset identifiers;

- feeder membership;

- section definitions;

- switch locations;

- configured network connectivity;

- customer-zone associations;

- normal device configuration.

The project will not attempt to reproduce geographic asset-management functionality.

The relevant role is to provide the configured model of the network against which operational states can be evaluated.

For example:

Section A2 is connected to Section A3.

Tie TS-01 connects A3 to B3.

Customer Zone CZ-A3 is supplied from A3.

This information changes relatively infrequently compared with live SCADA telemetry.

The separation between configured connectivity and live device state is also essential to the seeded topology defect, because the project must be able to demonstrate a situation in which correct live telemetry is processed against an incorrect network configuration.

# 9.3 ADMS Function

The ADMS representation will serve as the principal operational network-analysis function.

Its minimum responsibilities will be:

- combine configured connectivity with current device states;

- determine the active operational topology;

- determine section energisation;

- identify healthy de-energised sections;

- maintain awareness of the defined faulted section;

- identify a candidate restoration path;

- assess restoration permissive conditions;

- recalculate topology following switching operations.

ADMS therefore converts raw network and telemetry information into operational understanding.

Conceptually:

GIS configuration

+

SCADA state

↓

ADMS

↓

Operational topology

↓

Section energisation

↓

Restoration assessment

The ADMS representation will remain deliberately limited to the functions required by the selected validation scenario.

# 9.4 OMS Function

The OMS representation will convert network outage state into customer-impact information.

Its responsibilities will be limited to:

- receive or consume the current de-energised section set;

- associate those sections with customer zones;

- establish the current outage extent;

- calculate affected-customer count;

- update customer impact following restoration.

For example:

De-energised sections:

A2

A3

Customer mappings:

A2 → CZ-A2 → 310 customers

A3 → CZ-A3 → 185 customers

Affected customers:

495

The OMS representation will not include crew dispatch, customer notifications, estimated restoration times or call-centre functionality because those functions are not required by the work package.

The governing project specifically requires affected customers and outage behaviour to be demonstrated, but not a full commercial OMS implementation.

OT project vision.pdf

# 9.5 Engineering Validation Function

The engineering-validation function is separate from the simulated operational systems.

It will represent the graduate engineer’s work package and include:

- validation test cases;

- expected results;

- observed results;

- pass/fail status;

- supporting evidence;

- defect records;

- investigation notes;

- correction records;

- repeat-test results.

This is a deliberate design separation.

For example:

Operational event:

ADMS determined A3 energised.

Engineering validation record:

Expected A3 = DE-ENERGISED

Observed A3 = ENERGISED

Result = FAIL

The first describes system behaviour.

The second evaluates that behaviour against an engineering expectation.

The Project Definition explicitly assigns the graduate responsibility for executing tests, comparing expected and observed behaviour, recording results, investigating failures and repeating validation following correction.

# 10. Information Flow Design

The design will represent information movement through the operational environment rather than simply updating all application state simultaneously.

The principal information flows are described below.

## 10.1 Network Configuration Flow

Persistent network configuration originates from the network/GIS representation.

GIS / NETWORK CONFIGURATION

│

│ assets

│ connectivity

│ normal states

│ customer-zone relationships

↓

ADMS

ADMS uses this information as the structural basis for topology processing.

OMS also requires access to the customer-zone relationship, either directly or through the common network model.

## 10.2 Live Telemetry Flow

Live monitored device information flows through the conceptual SCADA function.

FIELD / PROTECTION

↓

SCADA

│

│ value

│ timestamp

│ quality

↓

ADMS

Examples include:

BRK-A

Value: OPEN

Quality: GOOD

Timestamp: current

and:

TS-01

Value: OPEN

Quality: GOOD

Timestamp: current

The design therefore treats telemetry as more than a single value.

## 10.3 Derived Topology Flow

ADMS combines configuration and operational state.

Configured connectivity

+

Current device state

↓

Operational topology

↓

Section energisation

The resulting derived state is then made available to other operational functions.

## 10.4 Outage Information Flow

OMS consumes the derived network state.

ADMS

│

│ de-energised sections

↓

OMS

│

│ customer-zone mapping

↓

Outage extent

Affected customer total

This keeps customer impact downstream of topology determination rather than directly linked to the initiating fault event.

## 10.5 Restoration Information Flow

Restoration assessment requires information from multiple functional domains:

Fault/isolation state

+

Operational topology

+

Telemetry validity

+

Feeder loading / capacity

↓

ADMS

↓

Candidate restoration assessment

The resulting assessment will expose both the decision and its engineering basis.

## 10.6 Event and Validation Flow

Operational activities will generate an event history.

Separately, validation tests will capture relevant operational evidence.

Operational systems

↓

Event record

↓

Referenced by

↓

Validation result

This allows a test result to point to the evidence that supports it without merging operational events and validation records into the same data concept.

# 11. Operational Fault Workflow Design

The selected feeder-fault scenario will be represented as a deterministic sequence of operational state changes and derived system responses.

The governing Project Definition fixes the core workflow as fault occurrence, breaker trip, topology update, de-energisation, alarm, outage identification, customer calculation, operator acknowledgement, restoration assessment, capacity check and event logging.

The proposed design decomposes that workflow as follows.

## 11.1 Initial Normal State

Before the fault:

- both feeder source breakers are closed;

- the normally-open tie is open;

- normal sectionalising devices are in their defined operating states;

- both feeders operate radially;

- all healthy network sections have valid source paths;

- all relevant customer zones are supplied;

- required telemetry is valid.

Conceptually:

SOURCE

├── BRK-A CLOSED → Feeder A → sections energised

│

└── BRK-B CLOSED → Feeder B → sections energised

A-side ─── TS-01 OPEN ─── B-side

# 11.2 Fault Initiation

A fault is introduced on the predefined fault section.

The precise section will be selected during the detailed Network Model stage.

Detailed fault-current behaviour is not simulated.

Instead:

FAULT occurs

↓

Protection operation assumed

↓

Affected feeder breaker trips

The protection operation is therefore an initiating condition, not a validation target.

# 11.3 Breaker State Change

The affected feeder breaker changes from:

CLOSED

to:

OPEN

SCADA receives and records the updated state.

The corresponding telemetry record must include a valid timestamp and quality state.

# 11.4 Alarm Generation

The feeder trip produces the relevant simulated operational alarm/event.

The alarm will contain enough information to identify:

- affected asset;

- alarm/event type;

- timestamp;

- current state;

- acknowledgement status.

The project does not need to reproduce sophisticated alarm management.

It needs to demonstrate that an appropriate alarm exists and that the operator can acknowledge it as required by the governing workflow.

# 11.5 Topology Recalculation

The breaker state change is supplied to the operational topology function.

ADMS combines:

configured network

+

BRK-A = OPEN

and recalculates which sections retain a path to an available source.

Any affected sections without such a path become:

DE-ENERGISED

This is a derived result.

# 11.6 Outage Identification

The OMS representation receives the set of de-energised sections.

It maps those sections to associated customer zones and calculates the outage impact.

The system will maintain both:

- the affected section set; and

- the resulting affected-customer total.

This ensures that the customer number remains explainable.

# 11.7 Alarm Acknowledgement

The operator acknowledges the relevant alarm.

Acknowledgement will create a traceable operational record identifying the action and time.

For the demonstrator, this provides a clear point of operator participation without attempting to model broader control-room procedures.

# 11.8 Fault Isolation

Before restoration can proceed, the identified faulted section must be isolated from the proposed alternate supply path.

The project will therefore represent appropriate sectionalising action.

After isolation, the design should distinguish:

FAULTED SECTION

= isolated and unavailable

from:

HEALTHY DE-ENERGISED SECTION

= possible restoration candidate

That distinction is central to the restoration workflow.

# 11.9 Candidate Restoration Identification

Once the fault is isolated, ADMS identifies the healthy de-energised portion that could potentially be supplied through the normally-open tie.

The proposed path is only a candidate.

For example:

Feeder B

↓

B-side section

↓

TS-01

↓

healthy A-side section

No restoration action is permitted merely because a physical path exists.

# 12. Restoration Design

Restoration will be represented as an explicit engineering assessment rather than a scripted switching action.

The governing Project Definition requires restoration to occur only where electrically valid and requires simplified checking of feeder loading, transferable load, alternate feeder capacity and resulting loading percentage.

The restoration design therefore uses a defined permissive sequence.

# 12.1 Restoration Permissive Conditions

The proposed restoration shall only be considered PERMITTED where all required conditions pass.

The conditions are:

### P1 — Fault isolated

The proposed restored path must not include the identified faulted section.

### P2 — Alternate source available

The alternate feeder must have an available source path through its closed source breaker and relevant network sections.

### P3 — Proposed topology valid

The switching arrangement must not create an unintended energised loop within the simplified radial network.

### P4 — Required telemetry valid

The switching-device states required to establish the proposed topology must be trustworthy and sufficiently current.

### P5 — Alternate feeder capacity sufficient

Existing feeder load plus transferred load must remain within the defined feeder capacity.

Only if all five pass is restoration permitted.

Formally:

RestorationPermitted = P1 \land P2 \land P3 \land P4 \land P5

# 12.2 Fault-Isolation Check

The restoration logic will verify that no active path from the alternate source passes through the faulted section.

If the fault is not isolated:

RESULT: REJECTED

Reason:

Faulted section remains connected to the proposed restoration path.

No tie operation should proceed.

# 12.3 Alternate-Source Check

The restoration path must lead to an available source.

For the alternate feeder this means, at minimum:

source available

AND

source breaker CLOSED

AND

continuous path to tie

If those conditions are not met:

RESULT: REJECTED

Reason:

Alternate source unavailable.

# 12.4 Topology-Validity Check

Because the simplified network normally operates radially, the proposed switching arrangement must not unintentionally establish simultaneous energised supply paths that create a loop.

The project will not calculate parallel power flows.

Instead, the topology engine will determine whether the proposed switching configuration violates the defined radial operating rule.

If so:

RESULT: REJECTED

Reason:

Proposed switching configuration creates invalid network topology.

# 12.5 Telemetry-Validity Check

Telemetry relevant to restoration will include:

value

quality

timestamp

The project will use three simplified quality states:

GOOD

UNCERTAIN

BAD

Telemetry will also be assessed for freshness against a defined project-specific threshold.

A required point is usable only where:

quality = GOOD

AND

age <= maximum allowed age

If necessary topology state cannot be established reliably, restoration shall be blocked rather than guessed.

For example:

RESULT: BLOCKED

Reason:

TS-01 telemetry stale.

Last known state: OPEN

Last update: 10:31:42

Age: 128 seconds

Maximum permitted age: 60 seconds

The exact threshold will be defined later as a project assumption/requirement rather than presented as an industry-standard value.

The Project Vision explicitly requires uncertain or stale telemetry to prevent unsafe actions.

# 12.6 Capacity Check

The simplified feeder-capacity assessment will use:

L_R = L_A + L_T

where:

- L_A = existing alternate-feeder loading;

- L_T = load proposed for transfer;

- L_R = resulting feeder loading.

The resulting loading percentage is:

Loading\% = \frac{L_R}{C_A} \times 100

where C_A is the defined alternate-feeder capacity.

Capacity passes where:

L_R \le C_A

and fails where:

L_R > C_A

The transfer load will not be a manually entered arbitrary number.

It will be derived from the simplified loads associated with the healthy de-energised sections included in the proposed alternate-supply path.

For example:

Healthy restorable sections:

A3 = 0.9 MW

A4 = 0.6 MW

Transferable load:

1.5 MW

This maintains the design chain:

topology

↓

restorable sections

↓

transferable load

↓

capacity calculation

↓

restoration decision

# 12.7 Restoration Assessment Outcomes

The design will distinguish three outcomes.

### PERMITTED

All required conditions have passed.

Example:

Fault isolated: PASS

Alternate source: PASS

Topology validity: PASS

Telemetry validity: PASS

Capacity: PASS

RESULT: RESTORATION PERMITTED

### REJECTED

Sufficient information exists to assess the proposal, but an engineering criterion fails.

Examples:

- alternate feeder capacity exceeded;

- fault not isolated;

- proposed topology invalid;

- alternate source unavailable.

### BLOCKED

The system cannot safely complete the assessment because required operational information cannot be trusted.

Example:

- stale tie-switch telemetry;

- BAD breaker-state quality.

This distinction prevents information uncertainty from being incorrectly represented as a confirmed engineering failure.

# 12.8 Simulated Restoration Execution

Where restoration is permitted, the demonstrator will allow the operator to initiate the corresponding simulated switching action.

The action will not represent autonomous authority to operate real electrical equipment.

Once the relevant tie/device states change:

device state changes

↓

topology recalculated

↓

section energisation recalculated

↓

OMS outage impact recalculated

Healthy restored sections should then become energised through the alternate feeder.

The faulted section remains isolated and de-energised.

# 12.9 Post-Restoration State

Following successful restoration, the application should clearly show:

- which sections remain out of service;

- which sections have been restored;

- which feeder currently supplies restored sections;

- resulting alternate-feeder loading;

- customers still affected;

- customers restored;

- operational events produced by the restoration sequence.

This creates evidence that the restoration changed the network state, not merely the user interface.

# 13. Seeded Defect Design

The intentional defect will be implemented as a network-model configuration error, not as a software fault deliberately coded to return the wrong result.

This follows the governing Project Definition, which requires one intentional configuration or data issue that causes validation to fail and then be investigated, corrected and revalidated.

The selected defect type is:

Incorrect topology connection within the configured distribution network model.

The exact incorrect relationship will be defined during the detailed Network Model stage, because it depends on the final section and switch arrangement.

The defect must satisfy the following design conditions:

- SCADA telemetry remains correct;

- the topology-processing logic remains correct;

- the incorrect network configuration causes at least one incorrect derived section-energisation result;

- the incorrect energisation propagates to an incorrect outage/customer-impact result;

- the root cause can be identified by tracing configuration rather than modifying software logic;

- correction of the configuration resolves the failure;

- the original failed validation can then be repeated successfully.

Conceptually:

Incorrect configured connectivity

↓

Normal topology algorithm

↓

Incorrect derived energisation

↓

Normal OMS calculation

↓

Incorrect affected-customer result

↓

Validation FAIL

This design is valuable because the operational applications can all behave exactly as configured while the overall engineering outcome is still wrong.

That supports the project’s focus on configuration and data investigation rather than arbitrary application debugging.

# 13.1 Defect Visibility

The defect should not be immediately obvious from the initial operational screen.

The expected investigation should begin with an observed validation mismatch such as:

Expected:

Section A3 = DE-ENERGISED

Observed:

Section A3 = ENERGISED

or:

Expected affected customers: X

Observed affected customers: Y

The engineer should then determine whether the discrepancy originates from:

- telemetry;

- topology derivation;

- customer mapping;

- or configured connectivity.

This ensures that the exercise demonstrates a structured investigation process rather than simply exposing a deliberately highlighted bad configuration field.

# 13.2 Defect Correction

Correction will modify only the relevant network configuration.

The topology-processing algorithm, OMS logic and validation logic should remain unchanged.

This allows the project to demonstrate a strong engineering principle:

A failed result caused by incorrect configuration should be corrected at the configuration source rather than masked through downstream application logic.

After correction, the same validation test will be repeated.

The corrected configuration should naturally produce:

Correct connectivity

↓

Same topology algorithm

↓

Correct energisation

↓

Same OMS logic

↓

Correct customer impact

↓

Validation PASS

# 13.3 Configuration Version Control

The project will preserve both defective and corrected configuration states.

A simple configuration-version model is sufficient, for example:

Network Model v1.0

Validation baseline

Contains intentional topology defect

Network Model v1.1

Corrected following defect investigation

The purpose is not to create a full enterprise configuration-management system.

The purpose is to preserve:

- which configuration was tested;

- which configuration failed;

- what was changed;

- why it was changed;

- and which corrected configuration subsequently passed.

This directly supports the project’s configuration-management and traceability objectives.

# 14. Operational Event and Audit Design

The demonstrator will maintain a chronological operational event history for significant system actions and state changes.

The event history will support reconstruction of what occurred during a validation scenario.

At minimum, an operational event should contain:

Event ID

Timestamp

Source function/system

Event type

Affected asset/entity

Description

Previous state/value where relevant

New state/value where relevant

Actor/origin where relevant

Example:

Event ID: EVT-0042

Timestamp: 10:32:14.218

Source: SCADA

Type: DEVICE_STATE_CHANGE

Asset: BRK-A

Previous: CLOSED

New: OPEN

Description: Feeder A breaker opened following protection operation

followed by:

Event ID: EVT-0043

Timestamp: 10:32:14.315

Source: ADMS

Type: TOPOLOGY_RECALCULATED

Description: Feeder A downstream energisation recalculated

and:

Event ID: EVT-0044

Timestamp: 10:32:14.427

Source: OMS

Type: OUTAGE_UPDATED

Description: Affected customer total recalculated

The governing Project Definition explicitly requires operational events to be recorded correctly, and the Vision requires engineering actions to remain traceable through system logs.

# 14.1 Operational Events Versus Engineering Validation Records

The design will maintain a deliberate separation between:

Operational event history
what the simulated OT environment did;

and:

Engineering validation evidence
how the graduate engineer assessed that behaviour.

For example:

Operational event:

ADMS marked A3 ENERGISED.

versus:

Validation observation:

Expected A3 = DE-ENERGISED

Observed A3 = ENERGISED

Result = FAIL

This distinction is important because a validation result is not itself an operational event.

# 15. Validation Support Design

The demonstrator must support repeatable validation rather than merely allow free-form interaction.

Each formal validation test should contain, at minimum:

Test ID

Related requirement(s)

Objective

Initial conditions

Required configuration version

Test steps

Expected result

Observed result

Pass / Fail

Evidence reference

Comments / findings

The exact test structure will be formalised later in the Validation Test Plan.

At design level, however, the demonstrator must make the required evidence observable.

# 15.1 Expected Versus Observed Behaviour

The validation interface or evidence package should make the distinction explicit.

For example:

Test: VT-TOP-003

Expected:

A1 = DE-ENERGISED

A2 = DE-ENERGISED

A3 = DE-ENERGISED

Observed:

A1 = DE-ENERGISED

A2 = DE-ENERGISED

A3 = ENERGISED

Result:

FAIL

The project should not automatically redefine the expected result based on what the implementation happened to produce.

Expected behaviour comes from the engineering requirements and network design.

Observed behaviour comes from execution.

# 15.2 Evidence Capture

Evidence should be sufficient to support later review without requiring the reviewer to reproduce every scenario manually.

Relevant evidence may include:

- network-state snapshots;

- telemetry records;

- topology state;

- outage/customer results;

- capacity calculation;

- restoration-permissive results;

- event-log entries;

- configuration records.

The project does not need sophisticated screenshot-management software.

The key requirement is that evidence can be clearly related to the test and conclusion it supports.

# 15.3 Repeatability

Validation scenarios must be capable of being reset to a defined initial state.

This is particularly important for:

- reproducing the intentional defect;

- applying the correction;

- rerunning the same test;

- demonstrating the before/after result.

The demonstrator should therefore support a controlled scenario-reset mechanism.

Conceptually:

Load defined network configuration

↓

Set normal device states

↓

Reset telemetry quality/timestamps

↓

Clear scenario events

↓

Execute validation

This does not require a complex simulation framework.

It requires only enough determinism that the same starting state produces the same expected behaviour.

# 16. Negative Validation Design

Not all successful tests should end with restoration being permitted.

Some tests should confirm that the system correctly prevents an unsafe or invalid action.

The most important negative validation case already established is stale or unreliable telemetry.

For example:

Tie telemetry:

Value = OPEN

Quality = GOOD

Age = 120 seconds

Maximum allowed age = 60 seconds

Expected:

Restoration assessment BLOCKED

If the system blocks restoration and identifies the stale point, the validation test passes.

This distinction is important:

Operational outcome: BLOCKED

Engineering test result: PASS

The project Vision explicitly requires uncertain or stale telemetry to prevent unsafe actions.

Other negative cases may be introduced later where they directly verify requirements, such as:

- insufficient feeder capacity;

- fault not isolated;

- alternate source unavailable;

- invalid topology.

These should remain targeted validation scenarios rather than becoming additional project storylines.

# 17. Demonstrator Design Principles

The demonstrator will be designed as an engineering-support interface.

It should help a reviewer answer questions such as:

- What is the current network configuration?

- Which devices are open or closed?

- Which sections are energised?

- Where is the fault?

- Which customers are affected?

- What telemetry is available and trustworthy?

- Why is restoration permitted, rejected or blocked?

- What events occurred?

- Which validation requirement is being tested?

- What failed?

- What configuration was corrected?

- Did repeat validation pass?

The interface should therefore prioritise clarity and traceability over visual sophistication.

This is directly aligned with the governing requirement that the interface exist to support the engineering process rather than showcase frontend development.

# 17.1 Proposed Demonstrator Areas

At design level, the demonstrator will likely require several logical views or panels.

### Network Overview

Displays:

- simplified single-line/network view;

- feeder/source state;

- breaker/switch positions;

- section energisation;

- faulted section;

- customer-zone impact.

### Telemetry / Operational State

Displays relevant monitored points including:

- value;

- quality;

- timestamp;

- freshness status.

### Alarm and Event View

Displays:

- active alarm;

- acknowledgement state;

- chronological event record.

### Restoration Assessment

Displays:

- candidate restoration path;

- fault-isolation check;

- alternate-source check;

- topology-validity check;

- telemetry-validity check;

- feeder-capacity calculation;

- final PERMITTED / REJECTED / BLOCKED outcome.

### Validation View

Displays:

- selected test case;

- related requirements;

- expected outcome;

- observed outcome;

- PASS/FAIL;

- evidence references.

### Defect / Configuration View

Supports inspection of relevant network configuration during the seeded-defect investigation.

This should not unnecessarily expose the answer before the investigation begins.

The exact screen structure is deferred until Step 8 — Demonstrator Design.

At this stage we are establishing what information must be available, not designing the UI.

# 18. Data Design Principles

Detailed database design is not part of this stage, but several data principles are already required.

## 18.1 Separate Configuration From Operational State

Configured network connectivity should not be stored as though it were live telemetry.

Likewise, current breaker/switch state should not overwrite the persistent network configuration.

Conceptually:

CONFIGURATION

assets

connections

customer mappings

capacity data

normal states

versus:

OPERATIONAL STATE

current device values

telemetry quality

timestamps

derived energisation

current outage

This separation is essential to the seeded defect.

## 18.2 Separate Observed From Derived Information

Examples of observed information:

breaker = OPEN

tie switch = CLOSED

Examples of derived information:

A3 = ENERGISED

customers affected = 185

Derived results should be recalculated when their underlying state changes rather than manually edited independently.

## 18.3 Maintain Stable Engineering Identifiers

Significant engineering entities should receive stable unique identifiers.

Examples:

FDR-A

BRK-A

SEC-A1

SW-A12

TS-01

CZ-A1

REQ-TOP-001

VT-TOP-001

EVT-00042

DEF-001

The exact naming convention will be defined later.

Stable identifiers will support traceability across documents, software, validation and defect reporting.

# 19. Design Assumptions

The current design relies on the following principal assumptions.

### DA-01

The upstream zone-substation source remains available during the selected feeder-fault scenario.

### DA-02

Protection correctly detects the predefined fault and opens the appropriate feeder breaker.

### DA-03

The faulted network section is known as part of the validation scenario; no fault-location algorithm is required.

### DA-04

The simplified network operates radially under normal conditions.

### DA-05

The alternate feeder can provide a valid restoration path to a healthy isolated portion of the affected feeder where restoration permissives are satisfied.

### DA-06

Simplified section loads and feeder capacities are sufficient for the project’s restoration-capacity assessment.

### DA-07

Customer impact can be adequately represented using aggregated customer zones attached to distribution sections.

### DA-08

The conceptual SCADA, GIS, ADMS and OMS functional boundaries are sufficient to demonstrate the required system interactions without representing a particular commercial implementation.

### DA-09

A project-specific telemetry age threshold will be established later for restoration validation.

These assumptions should eventually appear in the dedicated Engineering Assumptions Record and be updated if later design work changes them.

# 20. Design Constraints

The design remains subject to the following constraints:

- all utility information is fictional;

- the network is deliberately small;

- operational systems are conceptual;

- electrical analysis is simplified;

- no real equipment is controlled;

- no production cybersecurity or enterprise deployment is required;

- no commercial OT product is replicated;

- no detailed load-flow, fault-level or protection study is performed;

- only one intentional engineering defect is included;

- software functionality is limited to what supports the engineering work package.

These constraints are consistent with both the governing Project Definition and the locked Project Decisions.

# 21. Key Design Decisions

The Engineering Design Brief establishes the following major design decisions.

| ID | Design Decision |
| --- | --- |
| DD-01 | Use a small normally radial two-feeder distribution network with a normally-open tie. |
| DD-02 | Represent distribution sections as the principal units for topology, load, outage and restoration reasoning. |
| DD-03 | Derive section energisation from configured connectivity and current switching state. |
| DD-04 | Separate persistent network configuration from live operational telemetry. |
| DD-05 | Represent SCADA, GIS/network configuration, ADMS and OMS as conceptual functional boundaries. |
| DD-06 | Use ADMS functionality for topology processing, energisation and restoration assessment. |
| DD-07 | Use OMS functionality for outage extent and affected-customer calculation. |
| DD-08 | Represent customers as aggregated zones attached to distribution sections. |
| DD-09 | Require fault isolation before alternate restoration. |
| DD-10 | Assess restoration using isolation, alternate-source, topology, telemetry and capacity permissives. |
| DD-11 | Distinguish PERMITTED, REJECTED and BLOCKED restoration outcomes. |
| DD-12 | Use telemetry value, quality and timestamp for operational decision support. |
| DD-13 | Use simplified feeder loading and capacity arithmetic rather than detailed power-flow analysis. |
| DD-14 | Seed one incorrect topology connection as the intentional engineering defect. |
| DD-15 | Generate the failed outcome naturally from erroneous configuration processed by normal system logic. |
| DD-16 | Preserve defective and corrected configuration versions for repeatable validation. |
| DD-17 | Keep operational event history separate from engineering validation evidence. |
| DD-18 | Design the demonstrator as an engineering-validation tool rather than a software showcase. |

# 22. Design Summary

The proposed solution is a deliberately simplified representation of a distribution utility operational environment designed to support one graduate-level validation work package.

The solution combines:

fictional network configuration

+

live simulated telemetry

↓

operational topology processing

↓

section energisation

↓

outage/customer impact

↓

restoration assessment

↓

simulated switching

↓

operational evidence

↓

engineering validation

The network and operational applications are not intended to reproduce commercial utility systems.

Their purpose is to provide enough technical behaviour for the graduate engineer to demonstrate:

- understanding of a simplified distribution network;

- understanding of OT information flows;

- requirements-based validation;

- topology reasoning;

- simplified restoration analysis;

- telemetry-quality awareness;

- configuration investigation;

- controlled correction;

- repeat verification;

- and engineering traceability.

This remains consistent with the overarching project objective: to resemble a credible junior engineering contribution to an OT upgrade rather than a standalone software product.