# Step 5 — Simplified Network Model

Operational Technology Graduate Demonstration Project
Document: Simplified Network Model
Version: 0.1
Status: Draft

# 1. Purpose

This document defines the fictional electricity distribution network used by the Operational Technology validation work package.

The Network Model provides the engineering reference against which:

- operational topology will be determined;

- section energisation will be calculated;

- customer outages will be identified;

- restoration paths will be assessed;

- transferable load will be calculated;

- validation expectations will be established;

- and the intentional topology defect will be investigated.

The governing Project Definition requires a deliberately small network containing one zone substation, two primary feeders, several distribution sections, a normally-open tie, customer zones, simplified loads and simplified telemetry. The network must remain small enough to be completely understood while still supporting the relevant distribution-system concepts.

Accordingly, the network defined here is not intended to represent a real utility feeder. It is a fictional engineering model constructed specifically to support the defined validation scenario.

# 2. Network Modelling Principles

The model follows the engineering decisions established during Investigation and Design.

### NM-P01 — Normally Radial Operation

Both feeders operate radially under the normal network configuration.

Each distribution section therefore has one intended active source path during normal operation.

### NM-P02 — Topology-Based Energisation

Section energisation is not permanently assigned.

It is derived from:

configured connectivity + current switching-device states + available source.

### NM-P03 — Section-Based Abstraction

Distribution sections are the principal units used for:

- connectivity;

- fault status;

- energisation;

- load;

- restoration;

- and customer impact.

Individual conductors, poles and distribution transformers are not represented.

### NM-P04 — Aggregated Loads and Customers

Each section has:

- a simplified aggregate electrical load; and

- an associated customer zone containing an aggregate customer count.

These values are fictional but internally consistent.

### NM-P05 — Sectionalising Capability

Adjacent distribution sections are separated by sectionalising switches.

This provides a consistent switching structure across both feeders and allows portions of the network to be isolated independently where required.

For the selected fault scenario, SW-A12 and SW-A23 provide the switching boundaries required to isolate SEC-A2.

### NM-P06 — Consistent Entity Modelling

Network elements representing the same class of engineering entity shall use a consistent modelling structure and information set unless a specific engineering reason requires otherwise. Differences in configuration or behaviour shall arise from the characteristics of the individual entity rather than arbitrary differences in the model.

# 3. Intended Network Topology

The proposed network contains:

- one zone substation/source;

- two feeder source breakers;

- four sections on Feeder A;

- four sections on Feeder B;

- three sectionalising switches on each feeder;

- one normally-open tie between the remote ends of the two feeders.

The intended/correct topology is:

The diagram is schematic rather than geographic.

The two feeders now use the same basic structural pattern:

Source breaker

↓

Section 1

↓

Sectionalising switch

↓

Section 2

↓

Sectionalising switch

↓

Section 3

↓

Sectionalising switch

↓

Section 4

The fault and restoration scenario occurs on Feeder A, but the network itself is not structurally designed only around that fault.

# 4. Why Four Sections per Feeder?

Four sections on each feeder provide enough complexity to demonstrate the engineering scenario without making the network unnecessarily large.

Both feeders now use the same basic sectional arrangement.

Feeder A provides:

SEC-A1

healthy upstream

↓

SW-A12

↓

SEC-A2

faulted

↓

SW-A23

↓

SEC-A3

healthy downstream

↓

SW-A34

↓

SEC-A4

healthy downstream / tie-end

This gives the restoration workflow a meaningful result:

- SEC-A2 remains isolated;

- SEC-A1 can be returned to its normal Feeder A source;

- SEC-A3 and SEC-A4 can be restored from Feeder B.

Feeder B provides the corresponding structure:

SEC-B1

↓

SW-B12

↓

SEC-B2

↓

SW-B23

↓

SEC-B3

↓

SW-B34

↓

SEC-B4

tie-end

The Feeder B sectionalising switches are not all required to operate during the primary validation scenario. Their inclusion provides a coherent network structure and allows the operational topology model to represent switching devices consistently across both feeders.

No additional sections are required to satisfy the project objectives.

# 5. Zone Substation

## ZS-01 — Zone Substation

| Attribute | Value |
| --- | --- |
| Identifier | ZS-01 |
| Name | TasGrid East Zone Substation |
| Type | Zone substation / source |
| Operational role | Upstream source |
| Supplies | FDR-A, FDR-B |
| Source status | AVAILABLE |

The name is fictional.

Internal transformers, busbars and upstream transmission infrastructure are outside the model boundary.

For topology processing:

ZS-01 is treated as an available energised source.

# 6. Feeder Definitions

## FDR-A — East Ridge Feeder

| Attribute | Value |
| --- | --- |
| Identifier | FDR-A |
| Name | East Ridge Feeder |
| Source | ZS-01 |
| Source breaker | BRK-A |
| Normal operating state | Energised |
| Defined capacity | 5.5 MW |
| Normal connected load | 3.20 MW |
| Normal loading | 58.2% |
| Sections | SEC-A1–SEC-A4 |
| Sectionalising switches | SW-A12, SW-A23, SW-A34 |
| Scenario role | Faulted feeder |

Normal loading:

\frac{3.20}{5.50}\times100=58.2\%

## FDR-B — Riverbend Feeder

| Attribute | Value |
| --- | --- |
| Identifier | FDR-B |
| Name | Riverbend Feeder |
| Source | ZS-01 |
| Source breaker | BRK-B |
| Normal operating state | Energised |
| Defined capacity | 6.0 MW |
| Normal connected load | 4.20 MW |
| Normal loading | 70.0% |
| Sections | SEC-B1–SEC-B4 |
| Sectionalising switches | SW-B12, SW-B23, SW-B34 |
| Scenario role | Alternate restoration feeder |

Normal loading:

\frac{4.20}{6.00}\times100=70.0\%

The feeder ratings are fictional project values rather than claimed utility-standard ratings.

Their purpose is to support the simplified restoration-capacity assessment.

# 7. Feeder A Section Model

Feeder A is the affected feeder.

## SEC-A1

| Attribute | Value |
| --- | --- |
| Identifier | SEC-A1 |
| Name | East Ridge Section 1 |
| Feeder | FDR-A |
| Simplified load | 0.75 MW |
| Customer zone | CZ-A1 |
| Customers | 180 |
| Normal energisation | ENERGISED |
| Scenario status | Healthy |

## SEC-A2

| Attribute | Value |
| --- | --- |
| Identifier | SEC-A2 |
| Name | East Ridge Section 2 |
| Feeder | FDR-A |
| Simplified load | 0.95 MW |
| Customer zone | CZ-A2 |
| Customers | 220 |
| Normal energisation | ENERGISED |
| Scenario status | Designated fault section |

SEC-A2 is the predefined location of the project feeder fault.

This does not imply that the demonstrator calculates fault location. The fault section is supplied by the validation scenario.

## SEC-A3

| Attribute | Value |
| --- | --- |
| Identifier | SEC-A3 |
| Name | East Ridge Section 3 |
| Feeder | FDR-A |
| Simplified load | 0.85 MW |
| Customer zone | CZ-A3 |
| Customers | 260 |
| Normal energisation | ENERGISED |
| Scenario status | Healthy / restorable |

## SEC-A4

| Attribute | Value |
| --- | --- |
| Identifier | SEC-A4 |
| Name | East Ridge Section 4 |
| Feeder | FDR-A |
| Simplified load | 0.65 MW |
| Customer zone | CZ-A4 |
| Customers | 190 |
| Normal energisation | ENERGISED |
| Scenario status | Healthy / restorable |
| Additional role | Feeder A tie-end section |

# 8. Feeder A Load and Customer Check

Feeder A load:

0.75+0.95+0.85+0.65 = 3.20\text{ MW}

Feeder A customers:

180+220+260+190 = 850

Therefore the normal Feeder A state is:

Connected load:       3.20 MW

Connected customers:  850

Affected customers:   0

Following complete loss of the feeder before isolation or restoration:

SEC-A1 = DE-ENERGISED

SEC-A2 = DE-ENERGISED

SEC-A3 = DE-ENERGISED

SEC-A4 = DE-ENERGISED

Expected initial affected customers:

180+220+260+190=850

This provides a clear expected outage result for later validation.

# 9. Feeder B Section Model

Feeder B remains healthy during the principal fault scenario.

## SEC-B1

| Attribute | Value |
| --- | --- |
| Identifier | SEC-B1 |
| Name | Riverbend Section 1 |
| Feeder | FDR-B |
| Simplified load | 1.10 MW |
| Customer zone | CZ-B1 |
| Customers | 240 |
| Normal energisation | ENERGISED |

## SEC-B2

| Attribute | Value |
| --- | --- |
| Identifier | SEC-B2 |
| Name | Riverbend Section 2 |
| Feeder | FDR-B |
| Simplified load | 1.20 MW |
| Customer zone | CZ-B2 |
| Customers | 280 |
| Normal energisation | ENERGISED |

## SEC-B3

| Attribute | Value |
| --- | --- |
| Identifier | SEC-B3 |
| Name | Riverbend Section 3 |
| Feeder | FDR-B |
| Simplified load | 1.00 MW |
| Customer zone | CZ-B3 |
| Customers | 230 |
| Normal energisation | ENERGISED |

## SEC-B4

| Attribute | Value |
| --- | --- |
| Identifier | SEC-B4 |
| Name | Riverbend Section 4 |
| Feeder | FDR-B |
| Simplified load | 0.90 MW |
| Customer zone | CZ-B4 |
| Customers | 210 |
| Normal energisation | ENERGISED |
| Additional role | Feeder B tie-end section |

# 10. Feeder B Load and Customer Check

Normal Feeder B load:

1.10+1.20+1.00+0.90 = 4.20\text{ MW}

Normal Feeder B customer count:

240+280+230+210 = 960

Normal feeder loading:

\frac{4.20}{6.00}\times100 = 70.0\%

The feeder therefore has:

6.00-4.20=1.80\text{ MW}

of simplified available capacity before reaching its defined project limit.

The addition of sectionalising switches does not alter these load or customer values.

# 11. Restoration Transfer Load

The healthy downstream Feeder A sections proposed for alternate restoration are:

- SEC-A3 = 0.85 MW

- SEC-A4 = 0.65 MW

Therefore:

L_T=0.85+0.65

\boxed{L_T=1.50\text{ MW}}

Feeder B existing load is:

L_B=4.20\text{ MW}

Resulting Feeder B loading following transfer is:

L_R=4.20+1.50

\boxed{L_R=5.70\text{ MW}}

Resulting loading percentage:

\frac{5.70}{6.00}\times100 = \boxed{95.0\%}

Therefore:

Existing FDR-B loading       4.20 MW

Proposed transfer            1.50 MW

Resulting loading            5.70 MW

Defined capacity             6.00 MW

Resulting loading            95.0%

Capacity permissive          PASS

The remaining simplified feeder capacity following restoration is:

6.00-5.70=0.30\text{ MW}

The governing project requires this simplified feeder-loading, transferable-load, alternate-capacity and loading-percentage reasoning rather than a full power-system study.

# 12. Switching Devices

The network contains two feeder source breakers, six sectionalising switches and one normally-open feeder tie.

## BRK-A — Feeder A Source Breaker

| Attribute | Value |
| --- | --- |
| Identifier | BRK-A |
| Feeder | FDR-A |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Trips following SEC-A2 fault |

## BRK-B — Feeder B Source Breaker

| Attribute | Value |
| --- | --- |
| Identifier | BRK-B |
| Feeder | FDR-B |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Maintains alternate supply |

## Feeder A Sectionalising Switches

### SW-A12

| Attribute | Value |
| --- | --- |
| Identifier | SW-A12 |
| Connection | SEC-A1 ↔ SEC-A2 |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Upstream isolation boundary for SEC-A2 |

### SW-A23

| Attribute | Value |
| --- | --- |
| Identifier | SW-A23 |
| Connection | SEC-A2 ↔ SEC-A3 |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Downstream isolation boundary for SEC-A2 |

### SW-A34

| Attribute | Value |
| --- | --- |
| Identifier | SW-A34 |
| Connection | SEC-A3 ↔ SEC-A4 |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Normal Feeder A sectionalising device |

SW-A34 is not required to operate during the principal restoration sequence. It remains CLOSED while SEC-A3 and SEC-A4 are restored together through TS-01.

## Feeder B Sectionalising Switches

### SW-B12

| Attribute | Value |
| --- | --- |
| Identifier | SW-B12 |
| Connection | SEC-B1 ↔ SEC-B2 |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Normal Feeder B sectionalising device |

### SW-B23

| Attribute | Value |
| --- | --- |
| Identifier | SW-B23 |
| Connection | SEC-B2 ↔ SEC-B3 |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Normal Feeder B sectionalising device |

### SW-B34

| Attribute | Value |
| --- | --- |
| Identifier | SW-B34 |
| Connection | SEC-B3 ↔ SEC-B4 |
| Normal state | CLOSED |
| Monitored | Yes |
| Scenario role | Normal Feeder B sectionalising device |

These devices remain CLOSED during the principal Feeder A fault/restoration scenario.

Their states are nevertheless part of the network topology and therefore relevant to determining whether a continuous alternate-source path exists from BRK-B to TS-01.

## TS-01 — Feeder Tie Switch

| Attribute | Value |
| --- | --- |
| Identifier | TS-01 |
| Connection | SEC-A4 ↔ SEC-B4 |
| Normal state | OPEN |
| Monitored | Yes |
| Scenario role | Alternate restoration connection |

The complete switching arrangement is therefore:

FDR-A

ZS-01

│

BRK-A

│

SEC-A1

│

SW-A12

│

SEC-A2  ← FAULT

│

SW-A23

│

SEC-A3

│

SW-A34

│

SEC-A4

│

TS-01

│

SEC-B4

│

SW-B34

│

SEC-B3

│

SW-B23

│

SEC-B2

│

SW-B12

│

SEC-B1

│

BRK-B

│

ZS-01

This representation also makes the future alternate-source topology particularly clear: when TS-01 is closed, a valid path to SEC-A3 and SEC-A4 depends on the relevant Feeder B devices remaining CLOSED.

# 13. Normal Operating Configuration

Under normal operation:

| Device | State |
| --- | --- |
| BRK-A | CLOSED |
| SW-A12 | CLOSED |
| SW-A23 | CLOSED |
| SW-A34 | CLOSED |
| TS-01 | OPEN |
| SW-B34 | CLOSED |
| SW-B23 | CLOSED |
| SW-B12 | CLOSED |
| BRK-B | CLOSED |

All eight distribution sections are ENERGISED.

C denotes CLOSED.

Because TS-01 is OPEN, there is no active electrical path between the two feeders.

Each section therefore has exactly one intended active source path under normal conditions.

# 14. Customer Zones

The customer-zone mapping is:

| Customer Zone | Supplied Section | Customers |
| --- | --- | --- |
| CZ-A1 | SEC-A1 | 180 |
| CZ-A2 | SEC-A2 | 220 |
| CZ-A3 | SEC-A3 | 260 |
| CZ-A4 | SEC-A4 | 190 |
| CZ-B1 | SEC-B1 | 240 |
| CZ-B2 | SEC-B2 | 280 |
| CZ-B3 | SEC-B3 | 230 |
| CZ-B4 | SEC-B4 | 210 |

No individual customer records are required.

Affected customers are derived from the energisation state of their associated section.

# 15. Network Model Baseline Values

The fixed engineering values established by the current model are:

| Item | Value |
| --- | --- |
| Zone substation | ZS-01 |
| Primary feeders | 2 |
| Sections per feeder | 4 |
| Sectionalising switches per feeder | 3 |
| Normally-open feeder ties | 1 |
| Feeder A capacity | 5.50 MW |
| Feeder A normal load | 3.20 MW |
| Feeder A normal loading | 58.2% |
| Feeder A customers | 850 |
| Feeder B capacity | 6.00 MW |
| Feeder B normal load | 4.20 MW |
| Feeder B normal loading | 70.0% |
| Feeder B customers | 960 |
| Fault section | SEC-A2 |
| Fault isolation switches | SW-A12, SW-A23 |
| Healthy downstream restoration sections | SEC-A3, SEC-A4 |
| Tie switch | TS-01 |
| Tie endpoints | SEC-A4 ↔ SEC-B4 |
| Transferable load | 1.50 MW |
| Customers restored through alternate feeder | 450 |
| Resulting FDR-B load | 5.70 MW |
| Resulting FDR-B loading | 95.0% |
| Customers remaining affected after completed restoration | 220 |

The alternate restoration supplies:

SEC-A3 + SEC-A4

with customer count:

260+190=\boxed{450}

The faulted section SEC-A2 remains isolated, leaving:

\boxed{220\ customers}

affected after successful restoration.

SEC-A1, containing 180 customers and 0.75 MW of load, can be restored from the normal Feeder A source once SEC-A2has been isolated by opening SW-A12 and SW-A23 and the Feeder A breaker is returned to the appropriate simulated operating state.

This is a good breakpoint because we now have the actual intended network.

The next part is particularly important. We should define the network as a sequence of engineering states:

State N0 — Normal
→ State N1 — Post-fault/trip
→ State N2 — Fault isolated
→ State N3 — Healthy upstream section restored from Feeder A
→ State N4 — Restoration assessment
→ State N5 — Healthy downstream sections restored from Feeder B

Then we’ll define Network Configuration v1.0 (defective) and v1.1 (corrected), including the exact incorrect topology connection and what wrong state/customer result it produces.

That will effectively give us the answer key against which the future demonstrator and validation tests are measured.